## Cover
Owner: HINDALCO INDUSTRIES LIMITED Ahura Centre, 1st Floor, B Wing, Mahakali Caves Road, Andheri (East), Mumbai - 400 093, India
EPCM Contractor: W. L. GORE & ASSOCIATES (Pacific) Pte, Ltd. India Branch 703, A-Wing, 215 Atrium, Andheri Kurla Road, Mumbai 400059, India
Nominated Subcontractor - Engineering, Quality Control, Supervision: SMARTLuth Solution and Service Pvt. Ltd. Unit No: 503, 5th Floor, ECO Centre,. EM-4 Sector-V, Salt Lake City, Kolkata - 700091, India
Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant
Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System
CALCULATION FOR BOOSTER FAN SIZING AND STACK DRAFT & LOSS
ISSUED FOR |  | APPROVAL □ |  |  | INFORMATION □ | MANUFACTURING □ |  | CONSTRUCTION □ |  |  | AS-BUILT □
00 |  |  | First Issue |  |  |  | IR |  |  | IR |  | BCB
Rev. | Date |  | Description of revision |  |  |  | Prepared |  |  | Checked |  | Approved
Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant | [6 empty] | Drg. / Doc. No. : S21001- TS01 - 05HNC- 227202 (CALC)
Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System | [6 empty] | Gore Doc. No.: RPDU5.PG.030CALC |  |  |  | page | 1 | of | 3
FGD - CALCULATION FOR BOOSTER FAN SIZING & STACK D&L | [6 empty] | GORE Job : RPDU5 |  |  |  | Rev. : | 00
[7 empty] | File: |  | FGD - CALC FOR BOOSTER FAN SIZING & STACK D&L
This document is a property of W.L. GORE & ASSOCIATES (Pacific) Pte, Ltd. and it may contain trade secrets or privileged, undisclosed or otherwise confidential information. If you have received this document in error, you are hereby notified that any review, copying or distribution of it is strictly prohibited.

## Friction drop-500
PRESSURE DROP CALCULATION
[10 empty] | Length in Layout | [9 empty] | Length in Layout
| 1 | - | Individual suction duct to BF | [6 empty] | 27 | mtr |  |  | 6 | - | Not used
| 2 | - | Not used | [10 empty] | 7 | - | FGTR inlet portion duct |  |  |  | 3.5 | mtr
| 3 | - | Common suction duct to BF inlet | [6 empty] | 25 | mtr |  |  | 8 | - | Not used
| 4 | - | BF common discharge duct to MCU inlet | [6 empty] | 34 | mtr |  |  | 9 | - | Not used
| 5 | - | MCU portion duct | [6 empty] | 10 | mtr |  |  | 10 | - | Wet Stack |  |  |  | 10 | mtr
DUCT SIZING -
| Segment |  | Flow (m3/hr) |  | Flow (ft3/min) |  |  |  | Ac. Vel. (mps) |  |  | Duct Size (in) |  |  | Ac. Vel. (fpm) |  |  | a (in) | b (in) | a (mm) | b (mm)
| 1 |  | 293335 |  | 172517.9011 |  |  |  | 14.1389 |  |  | 70.9 x 126 |  |  | 2782.5412 |  |  | 70.8661 | 125.9843 | 1800 | 3200
| 2 |  | Not used
| 3 |  | 586669 |  | 345035.2141 |  |  |  | 13.0304 |  |  | 98.5 x 196.9 |  |  | 2564.3856 |  |  | 98.4252 | 196.8504 | 2500 | 5000
| 4 |  | 565433 |  | 332545.7732 |  |  |  | 12.5587 |  |  | 98.5 x 196.9 |  |  | 2471.5611 |  |  | 98.4252 | 196.8504 | 2500 | 5000
| 5 |  | 565433 |  | 345035.2141 |  |  |  | 9.0489 |  |  | 118.2 x 236.3 |  |  | 1780.8233 |  |  | 118.1102 | 236.2205 | 3000 | 6000
| 6 |  | Not used
| 7 |  | 479870 |  | 282223.9596 |  |  |  | 7.837 |  |  | 98.5 x 267.8 |  |  | 1542.3214 |  |  | 98.4252 | 267.7165 | 2500 | 6800
| 8 |  | Not used
| 9 |  | Not used
| 10 |  | 479870 |  | 282223.9596 |  |  |  | 14.8032 |  |  | 118.2 x 118.2 |  |  | 2913.2738 |  |  | 118.1102 | 118.1102 | 3000 | 3000
| DUCT EQUIVALENT LENGTH - | [15 empty] | EQUIVALENT LENTGH OF BENDS :
| Segment |  | Str. Lgth (ft) |  | 90 deg bend |  |  | Total Eq. Lgth (ft) | [9 empty] | Segment | l/Deq | Deq | Leq,ft
[5 empty] | No. | Eq. lgth
| 1 |  | 88.587 |  | 2 | 127.803 |  | 344.1931 | [9 empty] | 1 | 15 | 102.2424 | 127.803
| 2 |  | Not used | [14 empty] | 2 | Not used
| 3 |  | 82.025 |  | 1 | 187.4231 |  | 269.4481 | [9 empty] | 3 | 15 | 149.9385 | 187.4231
| 4 |  | 111.554 |  | 3 | 187.4231 |  | 673.8233 | [9 empty] | 4 | 15 | 149.9385 | 187.4231
| 5 |  | 32.81 |  | 1 | 899.6308 |  | 932.4408 | [9 empty] | 5 | 60 | 179.9262 | 899.6308
| 6 |  | Not used | [14 empty] | 6 | Not used
| 7 |  | 11.4835 |  | 1 | 860.9729 |  | 872.4564 | [9 empty] | 7 | 60 | 172.1946 | 860.9729
| 8 |  | Not used | [14 empty] | 8 | Not used
| 9 |  | Not used | [14 empty] | 9 | Not used
| 10 |  | 32.81 |  | 0 | 161.3925 |  | 32.81 | [9 empty] | 10 | 15 | 129.114 | 161.3925
DUCT PRESSURE DROP -
| Segment |  | Eq. Dia. (in) | Selected Dia. (in) | Area (ft2) |  | Vel(fpm) |  | Total Eq. Lgth (ft) |  |  |  | Friction Drop (in. wg)
| 1 |  | 102.2424 | 102.2424 | 57.0152 |  | 3025.8221 |  | 344.1931 |  |  |  | 0.24635 | [8 empty] | 1750
| 2 |  | Not used | [18 empty] | 2400
| 3 |  | 149.9385 | 149.9385 | 122.6181 |  | 2813.9013 |  | 269.4481 |  |  |  | 0.10592 | [8 empty] | 2400
| 4 |  | 149.9385 | 149.9385 | 122.6181 |  | 2712.0449 |  | 673.8233 |  |  |  | 0.24768 | [8 empty] | 2400
| 5 |  | 179.9262 | 179.9262 | 176.5701 |  | 1954.0981 |  | 932.4408 |  |  |  | 0.15111 | [8 empty] | 3275
| 6 |  | Not used | [18 empty] | 2400
| 7 |  | 172.1946 | 172.1946 | 161.7213 |  | 1745.1249 |  | 872.4564 |  |  |  | 0.12142 | [8 empty] | 4375
| 8 |  | Not used | [18 empty] | 2400
| 9 |  | Not used | [18 empty] | 2400
| 10 |  | 129.114 | 129.114 | 90.9233 |  | 3103.9784 |  | 32.81 |  |  |  | 0.018504 | [8 empty] | 1750
[7 empty] | Total drop in ducts | [5 empty] | 0.89098
| Friction drop in the path | [12 empty] | 0.89098 |  |  | in. wg
| Demister | [7 empty] | 25 | mmwc |  |  |  | 0.98425 |  |  | in. wg
| Pr. Drop in MCU (Assumed additional drop to duct drop) | [7 empty] | 5 | mmwc |  |  |  | 0.19685 |  |  | in. wg
| Pr. Drop in FGTR - 500 mg/nm3 case | [7 empty] | 1760 |  | Pa |  |  | 7.0633 |  |  | in. wg
| Expansion bellows (assumed) | [7 empty] | 1 | mmwc |  | 2 | nos | 0.07874 |  |  | in. wg
| Pr. Drop in dampers (assumed) | [7 empty] | 2 | mmwc |  | 2 | nos | 0.15748 |  |  | in. wg
| From Stack Calculation | [12 empty] | 0.67741 |  |  | in. wg
Not used
| Pressure drop along maximum length | [12 empty] | 10.049 |  |  | in. wg
| Margin | [12 empty] | 32% |  |  | %
| Pressure drop with margin | [12 empty] | 13.2647 |  |  | in. wg
[14 empty] | 336.9245 |  |  | mm wg
| Booster Fan suction head ( assumed ) | [12 empty] | -25 |  |  | mm wg
| Differential head of Fan | [12 empty] | 361.9245
| Fan head selected | [12 empty] | 362 |  |  | mm wg
Not used
| Flow | [12 empty] | 586669 |  |  | m3/hr
| Margin | [12 empty] | 15% |  |  | %
| Fan capacity calculated | [12 empty] | 674669.35 |  |  | m3/hr
| Fan capacity selected | [12 empty] | 674700 |  |  | m3/hr

## Friction drop-200
PRESSURE DROP CALCULATION
[10 empty] | Length in Layout | [9 empty] | Length in Layout
| 1 | - | Individual suction duct to BF | [6 empty] | 27 | mtr |  |  | 6 | - | Not used
| 2 | - | Not used | [10 empty] | 7 | - | FGTR inlet portion duct |  |  |  | 3.5 | mtr
| 3 | - | Common suction duct to BF inlet | [6 empty] | 25 | mtr |  |  | 8 | - | Not used
| 4 | - | BF common discharge duct to MCU inlet | [6 empty] | 34 | mtr |  |  | 9 | - | Not used
| 5 | - | MCU portion duct | [6 empty] | 10 | mtr |  |  | 10 | - | Wet Stack |  |  |  | 10 | mtr
DUCT SIZING -
| Segment |  | Flow (m3/hr) |  | Flow (ft3/min) |  |  |  | Ac. Vel. (mps) |  |  | Duct Size (in) |  |  | Ac. Vel. (fpm) |  |  | a (in) | b (in) | a (mm) | b (mm)
| 1 |  | 293335 |  | 172517.9011 |  |  |  | 14.1389 |  |  | 70.9 x 126 |  |  | 2782.5412 |  |  | 70.8661 | 125.9843 | 1800 | 3200
| 2 |  | Not used
| 3 |  | 586669 |  | 345035.2141 |  |  |  | 13.0304 |  |  | 98.5 x 196.9 |  |  | 2564.3856 |  |  | 98.4252 | 196.8504 | 2500 | 5000
| 4 |  | 565433 |  | 332545.7732 |  |  |  | 12.5587 |  |  | 98.5 x 196.9 |  |  | 2471.5611 |  |  | 98.4252 | 196.8504 | 2500 | 5000
| 5 |  | 565433 |  | 345035.2141 |  |  |  | 9.0489 |  |  | 118.2 x 236.3 |  |  | 1780.8233 |  |  | 118.1102 | 236.2205 | 3000 | 6000
| 6 |  | Not used
| 7 |  | 479870 |  | 282223.9596 |  |  |  | 7.837 |  |  | 98.5 x 267.8 |  |  | 1542.3214 |  |  | 98.4252 | 267.7165 | 2500 | 6800
| 8 |  | Not used
| 9 |  | Not used
| 10 |  | 479870 |  | 282223.9596 |  |  |  | 14.8032 |  |  | 118.2 x 118.2 |  |  | 2913.2738 |  |  | 118.1102 | 118.1102 | 3000 | 3000
| DUCT EQUIVALENT LENGTH - | [15 empty] | EQUIVALENT LENTGH OF BENDS :
| Segment |  | Str. Lgth (ft) |  | 90 deg bend |  |  | Total Eq. Lgth (ft) | [9 empty] | Segment | l/Deq | Deq | Leq,ft
[5 empty] | No. | Eq. lgth
| 1 |  | 88.587 |  | 2 | 127.803 |  | 344.1931 | [9 empty] | 1 | 15 | 102.2424 | 127.803
| 2 |  | Not used | [14 empty] | 2 | Not used
| 3 |  | 82.025 |  | 1 | 187.4231 |  | 269.4481 | [9 empty] | 3 | 15 | 149.9385 | 187.4231
| 4 |  | 111.554 |  | 3 | 187.4231 |  | 673.8233 | [9 empty] | 4 | 15 | 149.9385 | 187.4231
| 5 |  | 32.81 |  | 1 | 899.6308 |  | 932.4408 | [9 empty] | 5 | 60 | 179.9262 | 899.6308
| 6 |  | Not used | [14 empty] | 6 | Not used
| 7 |  | 11.4835 |  | 1 | 860.9729 |  | 872.4564 | [9 empty] | 7 | 60 | 172.1946 | 860.9729
| 8 |  | Not used | [14 empty] | 8 | Not used
| 9 |  | Not used | [14 empty] | 9 | Not used
| 10 |  | 32.81 |  | 0 | 161.3925 |  | 32.81 | [9 empty] | 10 | 15 | 129.114 | 161.3925
DUCT PRESSURE DROP -
| Segment |  | Eq. Dia. (in) | Selected Dia. (in) | Area (ft2) |  | Vel(fpm) |  | Total Eq. Lgth (ft) |  |  |  | Friction Drop (in. wg)
| 1 |  | 102.2424 | 102.2424 | 57.0152 |  | 3025.8221 |  | 344.1931 |  |  |  | 0.24635 | [8 empty] | 1750
| 2 |  | Not used | [18 empty] | 2400
| 3 |  | 149.9385 | 149.9385 | 122.6181 |  | 2813.9013 |  | 269.4481 |  |  |  | 0.10592 | [8 empty] | 2400
| 4 |  | 149.9385 | 149.9385 | 122.6181 |  | 2712.0449 |  | 673.8233 |  |  |  | 0.24768 | [8 empty] | 2400
| 5 |  | 179.9262 | 179.9262 | 176.5701 |  | 1954.0981 |  | 932.4408 |  |  |  | 0.15111 | [8 empty] | 3275
| 6 |  | Not used | [18 empty] | 2400
| 7 |  | 172.1946 | 172.1946 | 161.7213 |  | 1745.1249 |  | 872.4564 |  |  |  | 0.12142 | [8 empty] | 4375
| 8 |  | Not used | [18 empty] | 2400
| 9 |  | Not used | [18 empty] | 2400
| 10 |  | 129.114 | 129.114 | 90.9233 |  | 3103.9784 |  | 32.81 |  |  |  | 0.018504 | [8 empty] | 1750
[7 empty] | Total drop in ducts | [5 empty] | 0.89098
| Friction drop in the path | [12 empty] | 0.89098 |  |  | in. wg
| Demister | [7 empty] | 25 | mmwc |  |  |  | 0.98425 |  |  | in. wg
| Pr. Drop in MCU (Assumed additional drop to duct drop) | [7 empty] | 5 | mmwc |  |  |  | 0.19685 |  |  | in. wg
| Pr. Drop in FGTR - 200 mg/nm3 case | [7 empty] | 2160 |  | Pa |  |  | 8.6686 |  |  | in. wg
| Expansion bellows (assumed) | [7 empty] | 1 | mmwc |  | 2 | nos | 0.07874 |  |  | in. wg
| Pr. Drop in dampers (assumed) | [7 empty] | 2 | mmwc |  | 2 | nos | 0.15748 |  |  | in. wg
| From Stack Calculation | [12 empty] | 0.67741 |  |  | in. wg
Not used
| Pressure drop along maximum length | [12 empty] | 11.6544 |  |  | in. wg
| Margin | [12 empty] | 32% |  |  | %
| Pressure drop with margin | [12 empty] | 15.3837 |  |  | in. wg
[14 empty] | 390.7472 |  |  | mm wg
| Booster Fan suction head ( assumed ) | [12 empty] | -25 |  |  | mm wg
| Differential head of Fan | [12 empty] | 415.7472
| Fan head selected | [12 empty] | 416 |  |  | mm wg
Not used
| Flow | [12 empty] | 586669 |  |  | m3/hr
| Margin | [12 empty] | 15% |  |  | %
| Fan capacity calculated | [12 empty] | 674669.35 |  |  | m3/hr
| Fan capacity selected | [12 empty] | 674700 |  |  | m3/hr

## Stack D&L
Draft & Loss Calculation of Stack
Input Data
No. of chimney, N | [5 empty] | : | 1
Maximum outlet flue gas quantity per Boiler, q | [5 empty] | : | 401991 | Nm3/hr
Temperature of flue gas at stack inlet, Ti | [5 empty] | : | 53 | deg.C
Temperature of flue gas at stack exit, Tf |  |  |  |  | assumed |  | 48 | deg.C
Temperature of ambient air, Ta | [5 empty] | : | 40 | deg.C
Stack height (H) | [5 empty] | : | 57 | m
Calculation
Barometric pressure at plant conditions, B | [5 empty] | = | 28.9764 | in of Hg
Specific volume of flue gas at 1000oR and 1 atm, vbf | [5 empty] | = | 24.7 | ft3/lb
Flue gas temperature at stack exit, Tf | [5 empty] | = | 118.4 | deg.F
Average temperature of flue gas, Tg | [5 empty] | = | 122.9 | deg.F
Average specific volume of flue gas,
|  |  |  | vg [= vbf x (Tg + 460)/1000 x (30/B)] |  | = | 14.9062 | ft3/lb
Actual volume flowrate of flue gas at stack outlet,
|  | Qfg [= N x q x ((Tg - 32)/1.8 + 273)/273 x (30/B)] |  |  |  | = | 493179.6237 | m3/hr
[6 empty] | = | 17403101.6177 | ft3/hr
Specific volume of ambient air at 1000oR and 1 atm, vba | [5 empty] | = | 25.4 | ft3/lb
Temperature of ambient air, Ta | [5 empty] | = | 104 | deg.F
Specific volume of ambient air at 104 deg.F,
|  |  |  | va [= vba x (Ta + 460)/1000 x (30/B)] |  | = | 14.8317 | ft3/lb
Viscosity of flue gas at 122.9 deg.F, μ | [5 empty] | = | 0.05 | lbm/ft.hr
Diameter of stack is calculated as,
Di [= √((4 x Qfg)/(π x 3600 x V))]
Stack draft is given by, SD = (H/5.2) x (1/va - 1/vg), |  |  |  |  | in of H2O
Stack loss is given by, SL = (2.76/B) x (Tg/Di4) x (m/105)2 x (f x H/Di + 1), in of H2O
where,
| H | = | stack height above gas entrance, ft
| gc | = | conversion constant |  |  | = | 32.17 | lbm.ft/lbf.s2
| va | = | specific volume of ambient air, ft3/lb |  |  | = | 14.8317 | ft3/lb
| vg | = | average specific volume of flue gas, ft3/lb |  |  | = | 14.9062 | ft3/lb
| Tg | = | average absolute gas temperature, deg.R |  |  | = | 582.9 | deg.R
| Di | = | internal diameter of stack, ft
| m | = | mass flow rate of gas, lb/hr |  |  | = | 1167504.3046 | lb/hr
| f | = | friction factor
Stack velocity, V | [6 empty] | 54.12 | ft/s
[7 empty] | 16.5 | m/s
Diameter of stack, Di (ft) | [6 empty] | 10.6644 | ft
[7 empty] | 3.2514 | m
| Stack height (H) | [5 empty] | 186.96 | ft
a. Stack draft, SD (in of H2O) | [6 empty] | 0.012128 | in wc
[7 empty] | 0.30804 | mmwc
| Reynolds no., Re [=3600xVxDi/(vgxμ)] | [5 empty] | 2787791.9634
| Friction factor, f [Moody's diagram] | [5 empty] | 0.009
b. Stack loss, SL (in of H2O) | [6 empty] | 0.67741 | in wc
[7 empty] | 17.2061 | mmwc
Net stack draft (a - b), in of H2O | [6 empty] | -0.66528 | in wc
[7 empty] | -16.8981 | mmwc