|  |  | Owner: HINDALCO INDUSTRIES LIMITED Ahura Centre, 1st Floor, B Wing, Mahakali Caves Road, Andheri (East), Mumbai - 400 093, India |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | EPCM Contractor: W. L. GORE & ASSOCIATES (Pacific) Pte, Ltd. India Branch 703, A-Wing, 215 Atrium, Andheri Kurla Road, Mumbai 400059, India |  |  |  |  |  |
|  |  | Nominated Subcontractor - Engineering, Quality Control, Supervision: SMARTLuth Solution and Service Pvt. Ltd. Unit No: 503, 5th Floor, ECO Centre,. EM-4 Sector-V, Salt Lake City, Kolkata - 700091, India |  |  |  |  |  |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System Specification of Acid Concentration Plant ` ) ISSUED FOR; APPROVAL; INFORMATION; MANUFACTURING; CONSTRUCTION; AS-BUILT. |
| 00 | 10-12-2021 | First Submission | IR | IR |  |  | BCB |
| Rev. | Date | Description of revision | Prepared | Checked |  |  | Approved |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant |  |  | Drg. / Doc. No.: S21001-TS01-XXXX-XXXX |  |  |  |  |
| Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System |  |  | Gore Doc. No.: RPDU5.XXXX |  |  |  |  |
| Specification of Acid Concentration Plant |  |  | GORE Job No.: RPDU5 |  |  | Rev. : 00 |  |
|  |  |  | File: SPECFICATION OF ACID PLANT |  |  |  |  |
| This document is a property of W.L. GORE & ASSOCIATES (Pacific) Pte, Ltd. and it may contain trade secrets or privileged, undisclosed or otherwise confidential information. If you have received this document in error, you are hereby notified that any review, copying or distribution of it is strictly prohibited. |  |  |  |  |  |  |  |

`

CONTENTS – SECTION-1

CLAUSE. NO.	                              DESCRIPTION	  PAGE NO.

A.		GENERAL	  2

A-a		CODES AND STANDARDS	  2

A-b		SYSTEM DESCRIPTION	  2

A-c		SCOPE OF SUPPLY	  3

A-d		SCOPE OF SERVICES	  4

A-e		EXCLUSIONS	  5

A-f		TERMINAL POINT	  5

B.		DESIGN & CONSTRUCTION REQUIREMENT	  5

C.		QUALITY CONTROL & QUALITY ASSURANCE	  6

D.		INSPECTION & TESTING	  7

E.		DRAWINGS / DOCUMENTS TO BE SUBMITTED	  9

ANNEXURES

ANNEXURE-I	:    TECHNICAL DATA SHEET

ANNEXURE-II	:     STANDARD ELECTRICAL SPEC

ANNEXURE-IIa	:     SPEC FOR ELEC. MOTOR ACTUATOR.

ANNEXURE-IIb	:     SPEC FOR PLC

ANNEXURE-III 	:     COMMERCIAL TERMS & CONDITIONS

ANNEXURE-IV	:	TENDER SCHEME DRG

ANNEXURE-V	:	TENDER PLOT PLAN

ANNEXURE-VI	:	DETAIL DELIVERABLE LIST POST –ORDER.

ANNEXURE-VII	:	LIST OF MAKES

SECTION – 2	:	SPECIFICATION & DATASHEET OF TANKS

SECTION – 3	:	SPECIFICATION & DATASHEET OF PUMPS

- General

1) Hindalco Industries Limited (HIL)-Renusagar intends to install Flue Gas Desulphurisation Project (FGD) in their Unit-5 ,1 x 80 MW captive power Plant. While trapping Sox from flue gas Dilute H2SO4 solution shall be generated on continuous basis. The generated acid solution shall be sent to the Acid Plant for increasing the concentration of the acid solution and generated concentrated acid and recovered water.

2)   During the present phase of plant configuration SOx outlet concentration achieved for flue gas shall be 500mg/Nm3 and for this case dilute acid solution generated shall be as indicated below. During the next phase further SOx will be trapped and dilute acid solution generated shall enhance as indicated below. The scope of the present acid concentration plant shall be limited to the present case of 500 mn/Nm3  with a provision in terms of space in layout. Pumps and motors shall be selected with final capacity consideration i.e 200 mg/Nm3 case.

3)  This specification covers the design, engineering, manufacture, assembly, testing at manufacturer's works, supply and delivery to project site properly packed for transportation, including shop painting, freight, transit insurance, all taxes, duties, octroi, other charges/levies as applicable, supervision of erection, testing and commissioning at site of all materials and equipment inclusive of electrical as specified and as required for Acid Concentration Plant with Tanks and Pumps complete with all materials and accessories for safe and trouble-free operation of same.

- Codes and Standards : The design, manufacture, inspection and testing of the equipment covered under this specification shall conform, in general, to the standards and codes (latest editions) mentioned below:

- International Organisation for Standardisation (ISO);ISO3585/3586/3587/4704

- Bureau of Indian Standards (BIS)

- British Standards (BS); BS EN 1595

- American National Standards (ANSI).

- Steel Pipe Flanges & Flanged Fittings (ASME B 16.5)

- ASTM. Standards for materials

- API : American Petroleum Institute.

- ASME: American Society of Mechanical Engineers; ASME SEC VIII

- TEMA: Tubular Exchanger Manufacturer Association.

- In case of any contradiction between the above standards and data specification sheets, the stipulations in the data sheets shall prevail and shall be binding on the Supplier/ Bidder.

- System Description : The water saturated flue gas is passed through Flue Gas treatment tower where SOx gases are entrapped by the modules of tower and generates acidic water which trickles down and gets collected in the bottom hoppers. This collected liquid is 10% H2SO4 solution ( Sulphuric Acid solution) with also separated suspended fly ash particle in the flue gas. This acidic solution is filtered and sent to the Acid Concentration Plant(ACP). In the ACP, the feed solution shall undergo processes like Single stage / Mutlistage Evaporation, Distillation, Condensation , various heat exchanging to convert the feed solution to high concentration acid about 95% H2SO4 solution. The recovered water shall be neutralised and processed for return back to the main plant for further use as process water. The product concentrated acid shall be stored and suitably used by the purchaser either for internal use or for external use.

For the purpose of heating and distillation, steam as heat source shall be used and vacuum shall be generated through vacuum pumps , if required. For condensation purpose, lower temperature process fluid shall be used to recycle the heat for heating of feed liquid thereby saving energy. Additionally, for condensation, chilled water system shall be there, if required.

The acid concentration plant alongwith other accessories shall operate through PLC based control system.

- Scope of supply , and supervision of erection and commissioning :

The scope for Acid Concentration plant shall consist of :

1)Waste Water Tank, Concentrated Acid Tank and Recovered Water Tank. Separate section for specification and datasheet may be referred.

2)Acid Transfer Pump, Acid Loading Pump and Recovered Water Return Pump (All 1w+1s). Separate section for specification and datasheet may be referred.

Note – Recovered water tank and Recovered water return pump is indicated with consideration that recovered water is generated at atmposheric pressure. If it can be generated at higher pressure, so that it may be transferred to the main plant, then these may be omitted at later stage. Presently, bidder should offer Recovered Water Tank and Recovered water return pumps, as optional.

3)Single Stage or Multi Stage Distillation Units, as required.

4) Complete set of Pressure Vessels as required.

5) Distillation Columns, Reboiler Heater Exchanger, Acidic Condenser etc as required.

6) Complete Set of Process Circulating Pumps (1w+1s for each pumps) for above system with drives.

7) Vacuum Generating System with Vacuum pumps (1w+1s), as required.

8) Chemical dosing tank and chemical dosing pumps (1w+1s), if any required for neutralisation of recovered water.

9) Complete set of Structural steel required for housing the entire plant including platforms, handrails etc.

10) Steam and Condensate piping, control valve as required.

11) Complete Chilled water system including Refrigerant Compressors, Condenser / Cooling Tower, Expansion/ Throttling Valves, Evaporator units. Chilled water pumps complete with piping, valves and instruments.

12) All rotating equipment like Pumps and Compressor shall have One working and One stand-by option.

13) Not used.

14) Complete interconnecting pipes (along with supply of supports and structural steel), Valves and Instrumentation for the system. Complete instrumentation required for satisfactory and automatic operation of the plant shall be provided by the Bidder.

15) All utility pipelines and valves as required within the battery limit of supply.

16) All Instruments ( Flowmeters, Pressure Gauges, DP Gauges, Switches, Transmitters etc), instrumentation cables, JBs etc)

17) MCC panel with suitable Incomer and outgoing starter feeders for all motors & other loads; All drive motors, earthing, illumination, all power & control cables required within the package including those from panel to drive, , as required. Standard specifications for all Electrical items are described in a separate section, attached with this main specification.

18) PLC based operating control panel of all drives under scope , HMI station, touch screen operation, all instrument cables within package, including those from field instrument to the control panel.

16) Sets of foundation bolts, base plate, support plate, grounding pad, lifting lugs, eye bolts, for each and related equipment.

17) First fill of chemicals, lubricants and oil.

18) Set of special tools and tackles.

19) Mandatory spares if specified. Price of same shall be evaluated.

20) Erection and commissioning spares.

21) List of recommended spares with Unit Rate for three (3) years of trouble-free operation. The Price of Recommended spares shall not be evaluated.

- Scope of services :

The following services shall be provided by the bidder for all equipment and accessories listed above:

1)Control Room – GA / Assignment drawing shall be given by vendor. Civil design shall be done by purchaser.

2) Engineering of complete system and equipment & submission of all necessary documentation, drawings, civil assignment detail and operation and maintenance manuals.

3) Inspection and testing of all equipment at manufacturer's shop.

4) Supply and application of painting at shop.

5) Packing for road transportation as applicable.

6) Transportation of all equipment including transit insurance up to site.

7) Supervision of Erection and commissioning of items supplied.

8) Witnessing of Performance test of equipment at site and fulfilment

Of Guaranteed Data /Parameters.

- Exclusions :

Following items are out of scope of Bidder:

- Utility piping & valves beyond battery limit.

- Erection at site.

- Civil foundation work and Civil work for Control Room.

- Terminal Point :

The terminal point shall be as follows.

- Any Dosing system – At inlet of dosing tank.

- 10% Acid solution feed-At the inlet of Waste Recycle Tank. Refer scheme drg.

- Recovered water – At the common discharge header of Recovered water return pump. Refer scheme drg

- 95% Concentrated product Acid – At the outlet of common discharge of Acid Loading Pump. Refer scheme drg

- Steam System – At inlet to Acid plant battery limit.

- Steam Condensate system – At outlet of Acid plant battery limit.

- Cooling Tower Make up – At inlet to Acid plant battery limit.

- Chilled Water Make up - At inlet to Acid plant battery limit

- Instrument Air - At inlet to Acid plant battery limit

10) Electrical – Suitable single point 415V, 3-ph 4-wire, 50Hz power supply at the incomer of MCC (package vendor to define maximum load & suggest minimum cable size requirement for incomer). Any other voltage level power supply requirements will be arranged by the package vendor in scope.

- Design and construction requirements

1)For selection and sizing of equipment the technical data sheet (Annexure-1) may be referred.

2) Material of construction – The material of construction shall be minimum as indicated in the technical datasheet. However the bidder may select higher grade based on requirement of the specific function as deemed suitable.

3) Adequate margin shall be considered for selection and sizing of equipment.

4) PG Test and Performance Guarantee – Supplier shall demonstrate PG test for stipulated time as agreed with Purchaser and following shall be the minimum items :

a) Acid Concentration Plant capacity – As per Technical datasheet annexed.

b) Feed Acid Solution quality – As per Technical datasheet annexed.

c) Product Acid solution flow and quality – As per Technical datasheet annexed.

d) Recovered Water flow and quality – As per Technical datasheet annexed.

e) Utility Steam Requirement – Shall be guaranteed by Bidder.

f) Condensate return quantity - Shall be guaranteed by Bidder.

g) Power consumption - Shall be guaranteed by Bidder.

- Quality Control Plan (QCP)/ Quality Assurance Plan (QAP)

The Supplier shall be responsible for assuring that his and his sub-suppliers quality control program meets the specified requirements.

The Supplier shall develop a recommended Purchaser inspection point program. This program shall include the design, manufacturing, inspection and testing operations that the Supplier believes may be of interest to Purchaser in demonstrating product quality, whether performed in his own or his sub-suppliers' facilities.  The inspection point program shall be submitted to the Purchaser/Purchaser's Engineer within four weeks of Letter of Intent being issued.

Purchaser and/or his designated representative shall have full access to the Supplier's and sub Supplier's facilities and work area for reviewing conformance to the approved QCP/QAP and records and for witnessing of inspections and tests. Purchaser/Purchaser's Engineer shall be notified ten (10) working days if inspection is in India and twenty one (21) working days if inspection to be carried outside India prior to the start of the tests and inspection points as specified by Purchaser.

Supplier shall have methods in place to assure that items and services including subcontracted items and services, comply with this Specification.  Supplier shall describe these methods in his proposal.

All manufacturing, processing, testing and inspection operations affecting the equipment or material may be subject to surveillance by Purchaser or Purchaser's Engineer.

Prior to production, Supplier shall submit to Purchaser a fabrication sequence describing inspection and/or tests to be performed, for use in determining inspection points that Purchaser may desire to witness.  The Purchaser shall advise the Supplier, prior to production, of those fabrication steps and shop inspection points that the Purchaser desires to witness, and shall identify which of these points require work to be stopped pending written authorization to proceed from Purchaser/Purchaser's Engineer.

For fabrication steps and tests that Purchaser desires to witness, Supplier shall give ten (10) working days if in India and twenty one (21) working days if in abroad for notice of witness points, and fifteen (15) working days if in India and twenty eight (28) working days if in abroad for notice of hold points.  Notification of hold or witness points shall not be considered to have been given until Purchaser has acknowledged receipt of such notification.

In the event of non-conformance of materials or equipment, the Supplier is to prepare a `Non-conformance Report'.  This will be signed jointly by the Supplier and the Purchaser's Engineer.  Each Non-conformance Report shall be dealt with on a `VERY URGENT' basis.  All deviations from this Specification must be documented and referred to Purchaser for written disposition.

The Supplier shall indicate the name of the manufacturer and place of test and inspection for each equipment supplied by him in the offer.

- Inspection and Testing

# Given below a Standard Inspection and Testing requirement (ITR). The relevant test for the specified equipment shall be applicable as per this document

1)	The Supplier shall conduct all tests and inspections required to ensure that the equipment furnished shall conform to the requirements of this specification and in compliance with requirements of applicable Codes and Standards. The particulars of the proposed tests and the procedures for the tests shall be submitted to the Purchaser for approval before conducting the tests. The Purchaser's representative shall be given full access to all tests. The Supplier shall intimate the Purchaser well in advance (at least 15 days notice) so that if desired his representative can witness the test.

2)	Where stage inspection is to be witnessed by Purchaser, in addition to above, the Supplier shall submit to the Purchaser at the initiation of the contract, the detailed PERT-Chart showing the manufacturing programme and indicating the period where Purchaser or his authorised inspecting agency is required at the shop.

3)	Shop Tests

3-1)Material Test

i) 	All materials used for construction shall be of tested quality. Physical and Chemical tests of materials shall be conducted as per the relevant standards and test certificates shall be made available to the Purchaser. If demanded by Purchaser’s inspector, proof of use of only tested quality material shall be furnished.

ii) 	Where stage inspection is to be witnessed by Purchaser, all material test certificates shall be correlated and verified with the actual material used for construction by Purchaser’s inspector who shall stamp the material. In case mill test certificates for the materials are not available, the Supplier shall carry out physical and chemical tests at his own cost from a testing agency, approved by the Purchaser, as per the requirement of specified material standard. The samples for physical and chemical testing shall be drawn up in presence of Purchaser’s inspector who shall also witness the testing.

iii) 	All castings shall be sound, clean and free from porosity, blow holes, hard spots and other harmful defects.

iv) 	The equipment system components shall be subjected to non-destructive testing (NDT) like Radiography, Ultrasonic test, Magnetic particle test, Liquid penetration test etc. as required & QAP must be approved by the Purchaser before  all tests. The accepted limit shall be as stipulated therein. All components subjected to NDT shall be identified and stamped by Purchaser’s inspector on successful completion of testing.

v)	Control panel sequence tests to be done.

- During assembly all clearances and alignments shall also be checked and recorded.

- All major components shall be tested for chemical composition and mechanical strength.

3-2) Hydraulic Test

All pressure parts shall be hydraulically tested at shop as per relevant code and at not less than 150% of design pressure where not specified, prior to painting and lining, if applicable. The pressure parts shall be kept pressurised for at least one (1) hour at this test pressure, unless contradicted by the relevant  test code.

3-3)Dynamic Balancing Test

All rotating components and the assembly of the shall be subjected to dynamic balancing test, as applicable.

3-4)Test for capacity, pressure drop and efficiency of equipment shall be made as per manufacturer’s standard.

3-5)Performance Test at shop

Type test/routine test for the system / equipment shall be done for satisfactory performance in accordance with the relevant IS/BS/ASME or equivalent standard.

Tests shall be conducted with actual driver being furnished.

Reports and test certificates of the above tests shall be submitted to the Purchaser.

3-6) All drive motors shall be tested as per Electrical standards and codes.

4)Performance Test at Site – Given below are the general requirement of site test.

Applicable items shall be considered.

4-1) After the equipment along with all accessories are installed at site, the following tests shall be conducted at site by the supplier with his own calibrated testing equipment:

- To check capability of each equipment to deliver rated performance specified & guaranteed by the supplier.

- To check proper and continuously reliable operation of the control/regulation/sequence of the equipment furnished.

c)	To check proper operation, freedom from excessive temperature rise, unsatisfactory vibration noise.

d)	The tests shall be carried out for a minimum period of eight (8) hours or as directed by the Engineer.

e)	To check the loaded and unloaded shaft horse power (BHP)

f)	To check power (KW) drawn by the equipment

g)	The piping system shall be subjected to a leak test at 1.5 times the design pressure.

If the performance at field is found not to meet the requirement, the liquidated damages shall be applied.

- Documents/Drawings to be submitted along with the bid as “Must Items” for a responsive bid.

# E-1 Along with Bid

- Scope of supply without any ambiguity.

- PFD/ P&ID, Brief Datasheet, Technical Particulars of offered item(s).

- Drive list / SLD.

- Utility requirement.

- Plot Plan and Elevation drawing.

- MOC of major items / equipment.

- QAP.

- Guaranteed Performance Data and Power Consumption at full load / rated condition with Seal and signature of the company.

- Price Schedule.

- Delivery Schedule.

- Details of Commissioning manpower.

- Document submission schedule as per Deliverable List (post order) in Annexure.

- Terms of Payment.

- Deviation List if any. Without any deviation list, bid shall be construed exactly as per requirement of Scope Document / Technical Data Sheet.

- Catalogue of all equipment.

- List of commissioning and maintenance spares.

- Recommended Spare parts list for Three (3) year’ operation.

# E-2 Post Order

# Detail deliverable list is attached as annexure and also briefly indicated below :

- Design Calculation, P&ID, Operation & Control Philosophy,Technical Datasheet,    Technical Particulars of offered item(s) along with its constructional features and Performance detail.

- Drive list / SLD.

- Utility requirement.

- Dimensional General arrangement Drawings.

- Cross sectional Drawings with partlist and MOC.

- Structural General arrangement and detail drawings.

- Operation & Maintenance Manual.

- Civil assignment detail.

- QAP showing the Customer / Third Party Inspector (TPI) Hold Points.

- Drive Unit data sheet and data sheet of PLC based control panel.

- Weight data for erection & loading data (static & dynamic) for civil design by other.

- Material Test certificates shall be furnished.