# Annexure-2b-SPECIFICATION OF PLC AND WORK STATION

# Scope of Supply and Services

The Bidder is to supply hardware for Control System generally covered under the various section of this specification. The Quantity and technical requirement of each item shall be as per the text of the specification , data sheet and tender drawing if attached. The PLC shall cover the following functions of the plant

- Open Loop Control System (OLCS)

- Closed Loop Control System (CLCS)

- Sequence Interlock & Protection System

- Data Acquisition System

- Communication with third party system

- The PLC system shall comprise of the followings as minimum as regard to hardware and software:

- Operator WorkStation (Industrial PC) with 21” LCD Monitor, mouse, keyboard, and necessary hardware and software – One (1) no. as per Data sheet

- Engineering cum Operator WorkStation (Industrial PC) with 21” LCD Monitor, mouse, keyboard, and necessary hardware and software – One (1) no. as per Data sheet

- Printer - one (1) A3/A4 Inkjet color

- System software, HMI software and application software for real time 			operation.

- Other software necessary to build custom screens, graphics, display, 	trend, logs, calculations, historian, events.

- Redundant Controller modules with redundancy in CPU, Power supply 	and communication processors as per Data sheet.

- All type of Rack and Cabinets

- In addition, the following miscellaneous items are also to be included in the bid

- Control Room furniture - Table for placement of the operator’s stations, programming station and printer, Two no chairs for operators.

- Supply of grounding materials only for PLC System

- Installation and & Commissioning spares as required.

- Factory Acceptance Test

- Consumable required till handing over of the plant after performance test / site Acceptance Test

- All special tools and tackle, as required

- Calibration equipment / instruments, as required

# Exclusions

- All civil work in the control room including false flooring

- Control room lighting and air conditioning

- Laying and identification of field cables

- Field instrument installation and calibration

# General Information

The design philosophy for this acid concentration plant is based on Programmable Logic Control System which shall be configured to meet the following basic requirements.

    - High Availability

    - High Reliability

    - High Maintainability

The Programmable Logic Control System (PLC) is envisaged for safe and efficient operation

of entire Sulphuric Acid Concentration Plant

The PLC System shall have a proven record of successful operation in similar application for a minimum period of two years in India/abroad.

The system shall be able to operate satisfactorily from 15 deg C ambient temperature up to 45 Deg. C and 10% to 90% non-condensing humidity.

Design Criteria and Basis

- Following Electric voltage and frequency level shall be considered as given below

Raw Power:

Three Phase , 415V, 50 HZ, 0.8 pf

Single Phase, 50 HZ, 220 V AC

UPS Power: Shall be provided

# Technical Specification

| A | TECHNICAL REQUIREMENTS |
| --- | --- |
| A-1 | PLC for Silica Plant shall be of reputed make as per alternative make list specified in the data sheet. Redundancy level shall be as specified in the data sheet. |
| A-2 | PC-PLC based system shall have 1 no Operator station ( console) and 1 no Operator cum engineering console with independent electronics. 1 no. of Network printers shall be connected to these PC consoles. PCs shall be provided with anti virus software. |
| A-3 | Personal computer for operation, PLC configuration, engineering and fault diagnostics shall be as per data sheet.. Operating system for the PC shall be MS window based. |
| A-4 | MMI software for operator interface shall be also be window based 64 bit software with run time and development version both. MMI software shall have all the features for plant operation, monitoring, control & engineering/configuration. PLC programming software shall also be provided. Attached data sheet shall also be considered |
| A-5 | The system shall be programmed in general as per the logic diagram or ladder diagram to be prepared by the successful bidder after order based on operation and interlock philosophy of the plant. |
| A-6 | No single mode failure shall affect the system whenever redundant system configuration is specified. |
| A-7 | ## Programmable logic controller shall be able to operate satisfactorily in the worst ambient condition as stated elsewhere The system shall be installed in environmentally controlled control room unless specifically indicated otherwise. |
| B | ## INPUT / OUTPUT SUB SYSTEM |
| B-1 | The maximum number of Input/Output per I/O module shall be as per the count of Sulphuric acid Concentration Plant supplier with margin as specified in the data sheet. |
| B-2 | Each I/O shall be electrically isolated from external control circuit by suitable means. The minimum isolation level between I/O and logic circuit shall be 1000 V DC. Or as specified in the data sheet |
| B-3 | Each I/O shall be protected against the reversal of polarity of the power supply voltage to I/O. |
| B-4 | Each module shall have a LED for each I/O per channel to indicate the status of each Input/ Output. |
| C | PROCESSOR SUB SYSTEM |
| C-1 | The processor shall have capability to implement all the control functions required to execute the logic schemes. The size of the memory shall be sufficient for the storage of the programme instructions required by the logic schemes. |
| C-2 | Memory shall be non-volatile. In case volatile memory is provided, battery back-up shall be provided for a minimum of three months to keep the storage intact. A battery drain indication shall be provided at least one week before the battery gets drained. |
| C-3 | Since dual processor is specified, redundancy shall be provided such that in case of failure of main processor the standby processor shall take over automatically without any bumps. Redundancy shall be provided for complete processor sub-system including CPU, memory and power supply. In case of failure of complete processor system, output shall take fail safe state automatically. |
| C-4 | It shall be possible to generate the first out alarm output by the PLC. |
| D | ## PLC CONSOLE |
| D-1 | The PC based PLC console shall be used for programming, programme storage, fault diagnostics and alarm monitoring. It shall also be possible to use this for plant operation, whenever specified. |
| D-2 | The keyboard shall preferably be touch sensitive sealed type, easy to operate with each key clearly identified. It shall be provided with a lock and key to prevent any unintentional programme modification. |
| D-3 | It shall be possible to modify, add or delete the application programme online without affecting the output. |
| D-4 | It shall be possible to printout the Ladder/logic diagram on the PLC printer. In addition, printer shall also print the diagnostic messages and reports, shut down report, I/O map, process alarms etc. |
| D-5 | PC based console must be of current release and state of the art. |
| E | ## SYSTEM POWER SUPPLIES |
| E-1 | Programmable logic controller shall operate on uninterrupted power supply with following specification: |
|  | Voltage - 220V 10% Frequency - 50 Hz 3 Hz Switchover Time - 5 millisecond |
| E-2 | Each I/O rack shall be provided with a separate power supply. |
| E-3 | Each processor unit shall be provided with separate power supply |
| F | ## SELF DIAGNOSTIC |
| F-1 | The system shall have extensive set of self-diagnostic sub-routines which shall be able to identify the system failure at least upto module level. At local level, failure of a module shall be identified by an individual LED. |
| F-2 | Whenever auto-testing of I/O modules is specified, the testing software must be capable of detecting faults in case of normally open as well as normally close system. |

# Other Requirement

.

a	FACTORY ACCEPTANCE TEST (FAT): SUPPLIER shall 	submit 	their Factory Acceptance Test procedure for 	Purchaser’s / 	Consultant’s approval. The FAT shall be 	carried out based on 	approved FAT procedure by 	Purchaser / Consultant.

b	SUPPLIER shall submit the Quality Control test certificates to Purchaser / Consultant along with the FAT schedule. The above test shall be carried out as per supplier’s Quality Control and 	assurance procedures. The hardware shall be subjected to all 	applicable tests for reliability and the quality as per approved 	QA/QC plan and applicable codes & standards.

c	Supplier shall be responsible for System Configuration and Software Development as per the control philosophy, process write-up etc supplied by the Sulphuric Acid Concentration Plant supplier

# List of Documents / Drawings

The following are minimum requirement for approval / information 	and any other document / drawing required for engineering / information shall also be furnished.

1.	System configuration or architecture diagram

2.	Power consumption estimate

3.	Controller and bus loading calculations

4.	Bill of materials

5.	GA and IA drawing for all panels, consoles and printers

6.	FAT and SAT procedure

7.	Hardware & Software specification along with catalogs

9.	Detailed I/O List &I/O allocation

10.	Grounding/ Earthing drawings

11.	Loop drawings

12.	Logic Drawing

13.	Control room layout

14.	Nest/controller loading details

15.	Panel / console base frame details

16.	Final graphics`

17.	write up on remote monitoring system by corporate personnel

Annexure: 2b-1 : Data sheet of PLC

Annexure-2b-2: Data sheet of Work Station

ANNEXTURE-2b-1	; Technical Data Sheet of PLC

A       PLC (Programmable Logic Controller) : 1 No

| 01. | Make & Release: | As Given Below |
| --- | --- | --- |
| 02. | System Configuration: | PLC based control system with dual Central Processing Unit (CPU) configuration. |
| 03. | Redundancy: | Yes (HOT Redundancy) |
| a. | Controller : | Yes |
| b. | Power supply: | Yes |
| c. | Communication: | Yes |
| 04. | Analog Input (Channel/Module) : | 1 |
| 05. | Digital Input (Channel/Module) : | 16 |
| 06. | Analog Output (Channel/Module) : | 08 |
| 07. | Digital Output (Channel/Module) : | 16 |
| 08. | Scan time for digital and pulse inputs: | Not greater than 250 msec. |
| 09. | Scan time for analog inputs: | Not greater than 500 msec. |
| 10. | I/O Expandability: | Yes |
| 11. | Inputs / Output Isolation: | Optical isolation for all digital inputs & outputs and galvanic isolation/optical isolation for all analog inputs & outputs shall be provided. |
| 12. | Communication: | Communication between PLC MODULE / STATIONS and the OPERATORS STATIONS shall be conducted at High speed 100 MBPS (MIN) with Ethernet based Open Protocol with no collision feature to avoid Data jamming /overloading of the System |
| 13. | Power Supply: | 240 V AC (UPS) |
| 14. | TFT Size/Make /Model No.: | 22" colour TFT LCD monitor. |
| 15. | Printer/Make /Model No.: | N.A |
| 16. | Type of back-up battery: | VRLA |
| 17. | Data Memory: | 500 GB |
| 18. | Program Memory: | 512 MB |
| 10. | Controller Memory: | 128 MB |
| 20 | Scan Time for Inputs: | 1 SEC. MAX. |
| 21. | Number of instruction: | Configurable. |
| 22. | Programming from TFT: | Required |
| 23. | Spares: |  |
| a. | I/O Channels | 20% |
| b. | I/O Modules | 20% |
| c. | Spare Slots | 20% |

B      UPS (Uninterrupted Power Supply):

| 1. | Type: | Solid-state s.c.r. / power transis Tor & microprocessor controlled with Static and maintenance bypass switch |
| --- | --- | --- |
| 2. | Duty: | Continuous |
| 3. | Enclosure: | Sheet steel,with Ip42 protection class |
| 4. | Ambient temperature: | 50 deg.c maximum, 5 deg.c minimum |
| 5. | Cooling: | Natural convection or forced cooling using Redundant fans |
| 6. | Relative humidity: | 95% non-condensing |
| 7. | Inverter capacity: | Vendor to decide |
| 8. | Voltage - |  |
|  | A. Inverter input | 415 v |
|  | B. Nominal output | 240v ac, 50hz, 1 phase |
| 9. | Nominal frequency: | 50hz |
| 10. | Input frequency: | 45 to 53 hz |
| 11. | Input power factor: | 0.92 |
| 12. | Output : |  |
|  | A. Voltage | 240 v, 50 hz, 1 phase +/- 1.0% |
|  | B. Frequency | 50hz ± 0.5% |
|  | C. Load power factor | 0.8 |
|  | D. Waveform | Sine wave |
|  | E. Harmonic distortion | Less than 2% |
| 13. | Transient voltage regulation (on application or removal of 100% load) | :±2% |
| 14. | Time to recover from transient to normal voltage | :50 milliseconds |
| 15. | Overload capacity: | A. 125% of full load for 10 minutes |
|  |  | B. 150% OF FULL LOAD FOR 1 MINUTE |
| 16. | Synchronization limit: | A. 49 to 51 hz (factory set) |
|  |  | B. ADJUSTABLE FROM 48 TO 53 HZ AT FIELD |
| 17. | Rated output current at rated output voltage with current limit not operating | 200% at 100 millisecond |
| 18. | Protection: | Overload and short circuit |
| 19. | Efficiency: | Better than 80% |
| 20. | Static switch: | Built-in solid state scr, continuous rated, With natural or forced cooling using Redundant fans |
| 21. | Static switch capacity: | A. Equal to full load capacity of the Inverter for continuous operation |
|  |  | B. 125% overload at 0.8 p.f for 2 minutes |
|  |  | C. 1000% of continuous rating for 5 cycle |
| 22. | Static switch normal voltage | 240v ac, 50hz, 1 phase |
| 23. | Transfer time | 1/4 cycle |
| 24. | Manual bypass switch type | Maintained, make before break |
| 25. | Battery | Sealed maintenance free high Discharge battery of adequate capacity to Meet the requirement of ups, generally Conforming to is 10918 |
| 22. | Battery rack | Two tier |
| 23. | Charger | Built-in |
| 24. | Indication | A. Output load, battery capacity, frequency |
|  |  | B. Alarm for low battery, line fail, ups fail |
| 25. | Back up time | 60 minutes in case of i/p power fail |
| 26. | Battery check | Test button |
| 27. | Ups size | Vendor to decide |

C. INPUT/OUTPUT REQUIREMENT FOR PROCESS WITHOUT MARGIN

Digital Input						Bidder to Indicate

Digital Output						Bidder to Indicate

Analogue Input					Bidder to Indicate

Analogue Output					Bidder to Indicate.

D. GENERAL

Make				Mitsubishi/ Yakogawa/ Scheinder/Allen Bradely

Type				fully wired , latest generation with communication

port acceptable to other make PLC for communication.

Purpose	For operation and control of Sulphuric Acid Concentration Plant

Operation Philosophy

of Plant 			To be indicated by Acid Plant

| ANNEXURE-2b-2: DATA SHEET OF OPERATOR STATION ETC |  |  |
| --- | --- | --- |
| 4 4 A. | OPERATOR STATION/ENGINEERING STATION (PC BASED) |  |
|  | PROCESSOR | PENTIUM IV OR BETTER |
|  | CONFIGURATION | TOWER |
|  | INTERNAL CLOCK | 3.2 GHz |
|  | ARCHITECTURE | 32 BIT |
|  | OPERATING SYSTEM | WIN NT OR HIGHER |
|  | RAM | 512 MB OR BETTER |
|  | HARD DISK DRIVE | 80 GB SCSI OR BETTER |
|  | CACHE | 512 KB LEVEL 2 |
|  | FLOPPY DRIVE | 3 1/2" |
|  | DVD DRIVE | YES |
|  | AUDIO CONTROLLER | 16 BIT |
|  | VIDEO CARD | PCI |
|  | USB PORTS | 2 NOS(MIN) |
|  | OTHER COMMUNICATION PORTS | AS REQUIRED FOR NETWORK INTERFACE |
|  | MOUSE | OPTICAL |
|  | GRAPHIC ACCELERATOR CARD | MINIMUM 8 MB |
|  | NO.OF WORKSTATIONS | 5 |
|  | NO.OF ENGINEERING WORKSTATIONS | 1 |
| B | MONITOR FOR WORK STATION AND ENGINEERING WORK STATION |  |
|  | TYPE | LCD COLOUR MONITOR |
|  | SCREEN DIAGONAL | 21" FLAT |
|  | DISPLAY | VGA OR BETTER |
|  | RESOLUTION | 1024 X 768 OR BETTER |
|  | DEGREE OF PROTECTION | IP-30 |
|  | EXTERNAL CONTROLS | BRIGHTNESS, CONTRAST, HORIZONTAL / VERTICAL AMPLIFICATION & SHIFT |
|  | POWER SUPPLY | 240 V,50 Hz, 1 PHASE |
|  | AMBIENT TEMPERATURE | 0-50 0C |
|  | HUMIDITY | 95% NON-CONDENSING |
|  | VERSION | TO SUIT INDUSTRIAL APPLICATION |
| C | KEY BOARD FOR WORK STATION AND ENGINEERING WORK STATION |  |
|  | TYPE | FLAT SPILL PROOF MEMBRANE TYPE OR POSITIVE DEPRESSION TYPE |
|  | KEY LOCK | LOCKABLE TYPE PUSH BUTTON MOUNTED ON KEYBOARD |
|  | LIFE EXPECTANCY | 50 MILLION CYCLES PER KEY |
|  | VERSION | TO SUIT INDUSTRIAL APPLICATION |
| D | PRINTER |  |
|  | TYPE | A3 COLOR LASER JET PRINTER, 1 NO OF REPUTED MAKE |
|  |  | DOT MATRIX PRINTER-1 NO.OF REPUTED MAKE |
| E | HMI (F0R OWS/EWS BASED CONTROL SYSTEM) |  |
|  | FUNCTION TO BE PERFORMED FROM HMI | a. SELECTION OF AUTO/ MANUAL, OPEN/ CLOSE, SEQUENCE AUTO, START/ STOP OPERATION. |
|  |  | b. DYNAMIC MIMIC DISPLAY DEPICTING THE PROCESS. |
|  |  | c. ALARM MONITORING, REPORT & LOG GENERATION, PRINTING OF TRENDS ETC. |
|  |  | d. ON LINE / HISTORICAL TRENDING, HISTORICAL STORAGE AND RETRIEVAL OF DATA. |
|  | RESPONSE TIME | a. CALLING UP A MIMIC: 2 SEC OR BETTER |
|  |  | b. UPDATING STATUS SIGNAL IN MIMIC: 1 SEC OR BETTER |
|  |  | c. UPDATING VARIABLES IN A MIMIC: 1 SEC OR BETTER |
|  |  | d. ISSUANCE OF COMMAND TO OUTPUT: 1 SEC OR BETTER |
|  | TYPE OF DISPLAY REQUIRED | OVERVIEW, GROUP, POINT & TREND DISPLAY |
|  | REPORT GENERATION | AUTOMATICALLY AT PRESCRIBED TIME INTERVALS, OR ON DEMAND |
|  | SYSTEM SHALL PERMIT THE OPERATOR TO SPECIFY MINIMUM OF 5 SUMMARY LOGS EACH WITH MINIMUM OF 25 POINTS TO BE PRINTED ON DEMAND. |  |