## Sheet1
ANNEXURE-3S-1
Item No. | 1 | 2 | 3
Description of the Pumps | RECOVERED WATER RETURN PUMP | ACID LOADING PUMP | ACID TRANSFER PUMP
Design & Testing Standard | Relevant IS/API/BS/ASME/ANSI/ ASTM standard and Hydraulic Institute Standard
Tag No. | RWRP-1/2 | ALP-1/2 | ATP-1/2
LIQUID | 0.2% H2SO4 SOLUTION | 95% H2SO4 SOLUTION | 10% H2SO4 SOLUTION
Operating Temp. at Deg. C. | 45 | 45 | 65
Qty Reqd. | 02 Nos. | 02 Nos. | 02 Nos.
Pump Type | Horizontal Centrifugal pump with flooded suction | Horizontal Centrifugal pump with flooded suction | Horizontal Centrifugal pump with flooded suction
Installation | Outdoor
Rated Capacity (m3/hr) | 12 | 20 | Bidder to furnish
Total Dynamic Head (MLC) | 30 ;; (Tentative, To be finalised during detail engg) | 20 ;; (Tentative, To be finalised during detail engg) | Bidder to furnish
Head provided in MLC | Bidder to furnish
Pump Model | Bidder to furnish
Pumps Design and construction standard | IS/API/Hydraulic Institute Standard-USA / relevant ASTM/ISO/BS standard
Casing | Bidder to furnish
Shaft | Bidder to furnish
Shaft Sleeve | Bidder to furnish
Impeller | Bidder to furnish
Bearing and Bearing housing | Bidder to furnish
Sealing | Mechanical Sealing- Bidder to indicate material of seal.
Size (Suc x Del) mm NB | Bidder to furnish
Efficiency | Bidder to furnish
BKW | Bidder to furnish
Motor KW rating | Bidder to furnish
RPM | Bidder to furnish
Motor Make | Siemens/ABB/Equivalent
Motor Data Sheet | Bidder to furnish
NPSHR in MWC | Bidder to furnish
Performance Curve Capacity vs. Head, NPSHR, Power and Efficiency | Bidder to furnish
Counterflanges | Bidder shall supply all inlet and outlet counterflanges, with nuts , bolts and gaskets as per ANSI B 16.5 and material as per pump material.
Drive Motor | TEFC, Induction type, class F insulation but with temperature rise limited to that of class B, 415 V, 3-phase, 50 Hz, motor rating shall be 10% more than the maximum pump power requirement and be sized as per next higher frame size. Where DC Motor is mentioned, it shall be provided as per spec.
Protection | Suitable as per outdoor installation location of the pump as stated above
Accessories | Flexible coupling with guard, common steel base plate /structural frame for pump and its drive, Fixation Nuts and Bolts with the foundation
General Requirement | Equipment shall be properly epoxy painted against Sulphate environment. Pumps shall have rising head-capacity characteristic and suitable for parallel operation. Operating range of pumps shall be 70% to 130% of rated flow as minimum. Minimum flow thru’ the Pumps shall be 30% or less of rated flow
Testing Requirement | Performance testing of Pumps,NDT for Impeller, shaft and casing. Bidder to consider DP test for impeller and casing and UT for Shaft as minimum. Hydraulic Test shall be as per Hydraulic Institute Standard at a pressure of 150 % of shut off head of pump for 1 hour. Dynamic balancing test as per relevant ISO standard for Shaft and Impeller.
Guarantee Data which will attract penalty for non-fulfilment | 1. Specified Rated Capacity and Head of Pump.
2. Pump Efficiency at the duty point
3. Power Requirement at the motor terminal at the rated point operation of pump.