|  |  | Owner: HINDALCO INDUSTRIES LIMITED Ahura Centre, 1st Floor, B Wing, Mahakali Caves Road, Andheri (East), Mumbai - 400 093, India |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | EPCM Contractor: W. L. GORE & ASSOCIATES (Pacific) Pte, Ltd. India Branch 703, A-Wing, 215 Atrium, Andheri Kurla Road, Mumbai 400059, India |  |  |  |  |  |
|  |  | Nominated Subcontractor - Engineering, Quality Control, Supervision: SMARTLuth Solution and Service Pvt. Ltd. Unit No: 503, 5th Floor, ECO Centre,. EM-4 Sector-V, Salt Lake City, Kolkata - 700091, India |  |  |  |  |  |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System TECHNICAL SPECIFICATION OF BOOSTER FAN AND DRIVE WITH ACCESSORIES TECHNICAL SPECIFICATION OF BOOSTER FAN AND DRIVE WITH ACCESSORIES ` ) ) ISSUED FOR; APPROVAL; INFORMATION; MANUFACTURING; CONSTRUCTION; AS-BUILT. |
| 00 | 16.12.2021 | First Submission | IR |  | IR |  | BCB |
| Rev. | Date | Description of revision | Prepared | Checked |  |  | Approved |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant |  |  | Drg. / Doc. No.: S21001- TS01 - 05HNC- 227202 |  |  |  |  |
| Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System |  |  | Gore Doc. No.:RPDU5.PG.030 |  |  | page 1 of 7 |  |
| Technical Specification of Booster Fan and Drive with Accessories |  |  | GORE Job No.: RPDU5 |  |  | Rev. : 00 |  |
|  |  |  | File: Tech Spec of Booster Fan |  |  |  |  |
| This document is a property of W.L. GORE & ASSOCIATES (Pacific) Pte, Ltd. and it may contain trade secrets or privileged, undisclosed or otherwise confidential information. If you have received this document in error, you are hereby notified that any review, copying or distribution of it is strictly prohibited. |  |  |  |  |  |  |  |

`

CONTENTS

CLAUSE. NO.	                              DESCRIPTION	  PAGE NO.

A.		GENERAL	  3

A-a		CODES AND STANDARDS	  3

A-b		SYSTEM DESCRIPTION	  3

A-c	SCOPE OF SUPPLY AND SUPERVISION OF ERECTION AND COMMISSIONING	4

A-d		SCOPE OF SUPPLY	  4

A-e		SCOPE OF SERVICES	  4

A-f		EXCLUSIONS	  4

A-g		TERMINAL POINT	  5

B.		DESIGN & CONSTRUCTION REQUIREMENT	  5

C.		NOT USED

D.		NOT USED

E.		DRAWINGS / DOCUMENTS TO BE SUBMITTED	  9

F.		ENCLOSED

ANNEXURES

ANNEXURE-I	:	TECHNICAL DATA SHEET

ANNEXURE-II	:     TENDER LAYOUT

ANNEXURE-III	:     STANDARD SPEC FOR ELEC. MOTORS

ANNEXURE-IV 	:     COMMERCIAL TERMS & CONDITIONS

ANNEXURE-V      :     QUALITY CONTROL PLAN

- General

This specification covers the design, engineering, manufacture, assembly, testing at manufacturer's works, supply and delivery to project site properly packed for transportation, including shop painting, freight, transit insurance, all taxes, duties, octroi, other charges/levies as applicable, supervision of erection, testing and commissioning at site of all materials and equipment inclusive of electrical as specified and as required for Booster Fan and Electric Motor, Bearing Lubrication system , Multi-louvre Inlet Damper OR Radial Vane Control, Suction and Discharge Expansion joints, Instruments, Couplings, Baseframes, foundation bolts, Inlet and Outlet counterflanges withnuts, bolts, gaskets etc complete with all materials and accessories for safe and trouble-free operation of the fan.

- Codes and Standards : The design, manufacture, inspection and testing of the equipment covered under this specification shall conform, in general, to the standards and codes (latest editions) mentioned below:

- Bureau of Indian Standards (BIS)

- American Gear Manufacturers Association(AGMA).

- American National Standards (ANSI).

- Steel Pipe Flanges & Flanged Fittings (ASME B 16.5)

- ASTM. Standards for materials

- API : American Petroleum Institute

- ASME: American Society of Mechanical Engineers.

- In case of any contradiction between the above standards and data specification sheets, the stipulations in the data sheets shall prevail and shall be binding on the Supplier/ Bidder.

- System Description :

The existing system of each unit has 2 x 50 % ID fans handling the flue gas and discharging through chimney. From the common discharge duct of the ID fans, new ducts will be put with isolation dampers and with a common header duct shall be made to carry the total flue gas at the inlet of one new Booster Fan ( 1 x 100% ). The common discharge of booster fan shall be sent to the inlet of Mist Cooling unit for moisture saturation and reduction in temperature. In the Mist cooling Unit water shall be sprayed in mist form for evaporative heat exchange and thereby reducing flue gas temperature and achieving saturated condition. After the mist cooling unit, the flue gas shall be sent to the Reactor Tower to trap SOx. From the outlet of this reactor tower the flue gas shall be sent to the New Wet Stack. Thus there shall be 1 x 100% Booster fan the details of which is indicated in the following content of the specification.

- Scope of supply , and supervision of erection and commissioning :

The scope of supply under this specification for Fan shall be as follows :

- One (1w) no. Centrifugal type Booster Fan complete with Impeller with shaft and casing.

- Flexible Coupling with guard between Fan and and Motor.

- Bearing with bearing housing for drive end and non-drive end.

- Gland type Shaft Seal with packing or Forced sealing with inert gas.

- Multi-louvre inlet damper OR Radial Vane Control with pneumatic actuator.

- Non-metallic Expansion joints for Inlet and Outlet.

- Vibration monitoring units for Bearing for Fan, Motor, Gearbox and Fluid coupling..

- RTDs with transmitters for Bearing temperature monitoring for above.

- Electric Motor complete with all standard accessories and instruments.

- If forced lubrication is proposed, Complete lubrication system with 1w+1s Lub Oil pumps, tank, piping, valves, instruments etc shall be included in scope.

- Scope of supply – general :

The scope supply common for all pumps indicated above shall be as follows :

- Sets of foundation bolts, base frames, support plate, grounding pad, lifting lugs, eye bolts, protection guards etc.

- All inlet and outlet counterflanges with nuts, bolts and gaskets.

- Set of special tools and tackles.

- First fill of lubricants and oil.

- Mandatory spares if specified. Price of same shall be evaluated.

- Erection and commissioning spares.

- List of recommended spares with Unit Rate for three (3) years of trouble-free operation. The Price of Recommended spares shall not be evaluated.

- Scope of services :

The following services shall be provided by the bidder for all equipment and accessories listed above:

1) Engineering of equipment & submission of all necessary documentation, drawings, civil assignment detail and operation and maintenance manuals.

2) Inspection and testing of all equipment at manufacturer's shop.

3) Supply and application of painting at shop.

4) Packing for road transportation.

5) Transportation of all equipment including transit insurance up to site.

5) Supervision of Erection and commissioning of items supplied.

6) Witnessing of Performance test of equipment at site and fulfilment

Of Guaranteed Data /Parameters.

- Exclusions :

Following items are out of scope of Bidder:

- Flue gas ducts.

- Power and control cable beyond battery limit.

- Civil foundation.

- Terminal Point :

- At the inlet and outlet of counter-flanges .

- Power supply at motor terminal box.

- Design and construction requirements

1)For selection and sizing of equipment the technical data sheets (Annexure-1) may be referred.

2) Material of construction – The material of construction shall be minimum as indicated in the datasheets. However the bidder may select higher grade based on requirement of the specific function as deemed suitable.

3) Adequate margin shall be considered for selection and sizing of equipment.

4) The design shall incorporate such materials as to ensure reliability and high availability of the fan service under adverse conditions of corrosion in the flue gases. The fan casing and impeller blades shall be provided with suitable renewable wear resistant liners of proven design. Suitable proven arrangements shall be provided for prevention of corrosion of fan components.

5) For flow control, Booster Fan shall be provided with Multi-louvre inlet damper OR Radial Vane control.

6) The Booster Fan shall operate in tandem with the existing ID fan and control of the both shall be in cascade.

7) The design of fans shall ensure prevention of corrosion of areas coming in contact with flue gases, prevention of build-up on blades and erosion of blades and prevention of entrance of flue gas and condensate into interior of rotor and hub. All stationary parts coming in contact with flue gases shall be provided with suitable lining or made from corrosion resistant materials. The rotor shall be made from suitable steel. The material of the construction of fan components shall be so chosen as to give long life to obviate frequent repairs and replacement of parts.

8) Booster fan components such as blades, hubs, casing etc. shall be able to encounter the dust burden of the order of 120 mg/Nm3. The minimum wear life of Booster fan components shall not be less than 25000 hours of operation from the date of commissioning.

9) Fans shall be suitable for conditions of temperature profiles for flue gas treatment plant.

10) The fans shall be suitable for stable operation continuously at 40% turndown condition.

11) The fan shaft shall be designed in such a way that critical speed shall not fall within 125% of the operating speed. The fan should be statically and dynamically balanced.

12) The following characteristic curves of the fan shall be submitted:

a) Flow v/s Total pressure

b) Flow v/s power consumption

c) Flow v/s efficiency

13) Fan induced duct vibration due to flow pulsations shall be avoided through suitable design.

14) Overhang type impeller designs shall not be accepted. Shaft shall be carried in bearings on either side of impeller and shall be independent of casing.

15) Adequate temperature detectors and indicators shall be provided for remote and local monitoring of the bearing metal temperature of fan and motor. Suitable vibration sensor devices shall be provided for monitoring the fan/motor bearing vibrations from Control Room.

16) Noise shall be limited to maximum 85 dbA as measured at a distance of 1m.

17) For forced oil lubrication arrangement (if envisaged) for fans and drive motors, the complete pumping system with storage tanks, thermostats, coolers, strainers, filters, sight glasses, pressure gauges and separate pressure switches, flow gauges, differential pressure switches, dial thermometers and separate temperature switches, flow control valves etc. shall be furnished. The lube oil pumps and filters shall be 2x100% capacity with proper isolating valves etc. The system shall also include controls, starters, ammeters for lube oil pump motors, interlocks and protection for motors etc. for each fan and motor.

18) Fan bearing shall be provided with oil bath to prevent damage in case of complete loss of plant auxiliary power when the fans must coast down without power.

19) Not used

20) Electrical Requirements – Attached separately.

21) Performance Guarantee –

The following parameters shall be guaranteed - Rated capacity, Rated Head, Efficiency at design point and power consumption at the rated point at motor terminal.

Supplier shall demonstrate PG test for stipulated time as agreed with Purchaser and following shall be the minimum items. PG test shall be minimum for 8 hours. Penalty for non-performance etc are indicated in Annexure-5.

- Not used

- Not used

- Documents/Drawings to be submitted along with the bid as “Must Items” for a responsive bid.

- Scope of supply without any ambiguity.

- Technical Datasheet, Performance curves,  of offered item(s) along with its constructional features and Performance detail.

- Drive list / SLD.

- Utility requirement.

- Dimensional General arrangement Drawings.

- Cross sectional Drawings with partlist and MOC.

- Civil assignment detail

- QAP showing the Customer / Third Party Inspector (TPI) Hold Points.

- Guaranteed Performance Data and Power Consumption at full load / rated condition with Seal and signature of the company. Scope of supply without any ambiguity.

- Drive Unit data sheet.

- Price Schedule.

- Delivery Schedule.

- Terms of Payment.

- Deviation List if any. Without any deviation list, bid shall be construed exactly as per requirement of Scope Document / Technical Data Sheet.

- Catalogue of all equipment.

- Recommended Spare parts list for Three (3) year’ operation.

- Weight data for erection & loading data (static & dynamic) for civil design by other.

- Material Test certificates shall be furnished after placement of Order.