Annexure-1 – Technical data sheet

- Flue gas parameters :

- Flue gas analysis ( % by weight, wet ) : CO2 – 18.86 ; SO2 – 0.12; N2 – 69.78 ; O2 – 5.43 ;  H2O – 5.82

- SPM – 120 mg/Nm3

- SOx level mg/Nm3 : 1246.00

- Technical details of Fan :

|  | Present Case | Future Upgradation case |
| --- | --- | --- |
| Booster Fan selection criteria | Fan shall be selected as per the present case indicated with the condition that by changing the impeller, motor or even casing, the fan can be upgraded for the future upgradation requirement as indicated. The load data for civil foundation design shall be provided considering the final upgraded fan load details. |  |
| Booster Fan Capacity, m3/hr | 6,74,700.00 | 6,74,700.00 |
|  | Above flow figures are at (-) 25mmwg at the tapping point and 148 deg C. |  |
| Pressure at tapping point of suction duct with existing discharge duct of existing ID fan | ( - ) 25 mmwg | ( - ) 25 mmwg |
| Estimated Loss of new suction duct upto new Booster Fan suction | 57 mmwg | 57 mmwg |
| Estimated Pressure at Booster Fan suction | (-)27-57 = (-)82 mmwg | (-)27-57 = (-)82 mmwg |
| Estimated Pressure at Booster Fan discharge required, mmwg | 331 mmwg | 384 mmwg |
| Booster Fan Differential Head, mmwg | 413.00 | 466.00 |
| Operating temp, degC | 148 | 148 |
| Qty - Nos | 01 (One ) | ------ |
| Type of Fan | Centrifugal with Backward or Radial Blades. |  |
| Fan arrangement | Fan to be simply supported, double inlet – single outlet type. Fan Inlet / Outlet orientation shall be as per layout attached as annexure. |  |
| Design Pressure | Fan housing design pressure shall be shut-off head of the fan. |  |
| Design Standard | Bidder to indicate |  |
| Testing Standard | Bidder to indicate |  |
| Tolerance | No negative tolerance on flow and head and no positive tolerance on absorbed power is allowed. |  |
| Guarantee | Flow , Head and Power consumption to be guaranteed. |  |
| Fan Control | Fan control shall be by Radial Vane Control or Multilouvre Damper Control with pneumatic actuated cylinders |  |
| Material- Casing | IS 2062 GR B ; If Liner to be provided bidder to indicate. |  |
| Material- Impeller | IS 2062 GR B |  |
| Material- Liner | Impeller shall be provided with abrasion resistant Liner of high BHN steel like SAILMA / TISCRAL; Bidder to indicate. |  |
| Material-Shaft | EN-8 / BS 970 / 83-080M40 / IS 1570 40C8 ; Bidder to indicate |  |
| Bearing and Bearing Housing type and material | Bidder to indicate |  |
| Sealing arrangement | Bidder to indicate |  |
| Bearing Lubrication | Bidder to indicate ; If forced lubrication is proposed, the lubrication system should be 1w +1s. |  |
| Cooling water requirement, m3/hr | Bidder to indicate |  |
| Instrument Air requirement, Nm3/hr at 6.0 bar g | Bidder to indicate |  |
| Instruments | Bidder to indicate. Fan and Motor Bearing temperature indicator and Vibration Monitoring arrangement shall be included. |  |
| Efficiency | Bidder to indicate |  |
| BKW | Bidder to indicate |  |
| Motor KW rating | Bidder to indicate |  |
| RPM | Preferred RPM is 1000. However bidder may speed to suit their fan curves. |  |
| Motor make | Bidder to indicate |  |
| Motor spec | As per separately attached spec |  |
| Motor datasheet | Bidder to indicate |  |
| Performance Curves – Capacity vs Head; Power and Efficiency | Bidder to indicate |  |
| Accessories | RVC/DDC , Base frame for Fan & Drive , Coupling, Foundation and Fixing bolts, Complete Lubrication system. |  |
| General Requirement | Equipment shall be properly epoxy painted against Sulphate environment. |  |