Annexure-1

Technical Data Sheet for Ash Filters

| Description | Ash Filter-A for Wash Recycle Pump- Common Line | Ash Filter-B for Wash Recycle Pump- Misting Line | Ash Filter for Wash Water Transfer Pump |
| --- | --- | --- | --- |
| Quantity | Two (02) ( 1W + 1S ) | Two (02) ( 1W + 1S ) | Two (02) ( 1W + 1S ) |
| Tag | 50HSM10AT003/4 | 50HSM10AT005/6 | 50HSM10AT007/8 |
| Liquid handled | Acidic water ( 10% conc ) H2SO4 solution with suspended ash particles | Acidic water ( 10% conc ) H2SO4 solution with suspended ash particles | Acidic water ( 10% conc ) H2SO4 solution with suspended ash particles |
| Type | Vertical cylindrical with dished ends | Vertical cylindrical with dished ends | Vertical cylindrical with dished ends |
| Location | Outdoor | Outdoor | Outdoor |
| Design Rated Service Flow Rate in m3/hr | 53.0 | 35.0 | 12.0 |
| Time Period for each Service Cycle between two consecutive backwash, in hrs | 24 preferable. However Bidder to indicate to optimize selection. | 24 preferable. However Bidder to indicate to optimize selection. | 24 preferable. However Bidder to indicate to optimize selection. |
| Volume of treated water between two consecutive backwash (Net), in m3 | As above. | As above. | As above. |
| Design surface flow rate in during filtering m3/m2/hr | Bidder to indicate. | Bidder to indicate | Bidder to indicate. |
| Design surface flow rate in during backwash m3/m2/hr | Bidder to indicate. | Bidder to indicate | Bidder to indicate. |
| Design Temperature in o C | 60.0 | 60.0 | 60.0 |
| Design Pressure , kg/cm2 g | 10.0 | 10.0 | 10.0 |
| Design Inlet TSS, ppm | 150 (maximum) | 100 (maximum) | 150 (maximum) |
| Design Outlet TSS , ppm | Less than 5. | Less than 5 | Less than 5. |
| Particle size , micron | 20.0 | 5.0 | 20.0 |
| Design Code | Bidder to indicate | Bidder to indicate | Bidder to indicate |
| Code for Tests and Inspections | As per the requirements of Tender Specification. | As per the requirements of Tender Specification | As per the requirements of Tender Specification. |
| Filter Media Type | Bidder to indicate. | Bidder to indicate. | Bidder to indicate. |
| Filter Media Depth | Bidder to indicate. | Bidder to indicate. | Bidder to indicate. |
| Percentage freeboard | 30 % minimum. | 30 % minimum | 30 % minimum. |
| Pressure drop across the filter ( Clean ) | Bidder to indicate | Bidder to indicate | Bidder to indicate |
| Pressure drop across the filter ( Before backwash ) | Bidder to indicate | Bidder to indicate | Bidder to indicate |
| Material of construction |  |  |  |
| Shell | PP( Polypropylene) lined FRP ( Fibre Reinforced Plastic ) | PP( Polypropylene) lined FRP ( Fibre Reinforced Plastic ) | PP( Polypropylene) lined FRP ( Fibre Reinforced Plastic ) |
| Dished ends | PP lined FRP | PP lined FRP | PP lined FRP |
| Thickness | Bidder to indicate | Bidder to indicate | Bidder to indicate |
| Manhole | One (1) no. of flanged nozzle and minimum 500 mm diameter. | One (1) no. of flanged nozzle and minimum 500 mm diameter. | One (1) no. of flanged nozzle and minimum 500 mm diameter. |
| Hand hole | Bidder to indicate | Bidder to indicate | Bidder to indicate |
| Pipe and fittings | PP( Polypropylene) | PP( Polypropylene) | PP( Polypropylene) |
| Valves | PP( Polypropylene), Flanged type with Counterflanges | PP( Polypropylene), Flanged type with Counterflanges | PP( Polypropylene), Flanged type with Counterflanges |
| Instruments | Minimum as per Tender P&ID and Bidder to indicate | Minimum as per Tender P&ID and Bidder to indicate | Minimum as per Tender P&ID and Bidder to indicate |
| Nozzles : | ( NB ) / QTY ( nos.) / PROJ. (mm ) /RATING | ( NB ) / QTY ( nos.) / PROJ. (mm ) /RATING | ( NB ) / QTY ( nos.) / PROJ. (mm ) /RATING |
|  | Sizes are indicative for tendering purpose | Sizes are indicative for tendering purpose | Sizes are indicative for tendering purpose |
| Inlet | 100 NB/01/150/ 150 lb | 80 NB/01/150/ 150 lb | 50 NB/01/150/ 150 lb |
| Outlet | 100 NB/01/150/ 150 lb | 80 NB/01/150/ 150 lb | 50 NB/01/150/ 150 lb |
| Manhole | 500 / 01 / 100 / 150 lb | 500 / 01 / 100 / 150 lb | 500 / 01 / 100 / 150 lb |
| Handhole | 150 / 01 / 100 / 150 lb | 150 / 01 / 100 / 150 lb | 150 / 01 / 100 / 150 lb |
| Vent | 40 / 01 / 100 / 150 lb | 40 / 01 / 100 / 150 lb | 40 / 01 / 100 / 150 lb |
| Backwash Inlet | Bidder to indicate / 150 lb | Bidder to indicate / 150 lb | Bidder to indicate / 150 lb |
| Backwash Drain | Bidder to indicate / 150 lb | Bidder to indicate / 150 lb | Bidder to indicate / 150 lb |
| Sample port (on pipeline) | 15 / 02 / 100 / 150 lb | 15 / 02 / 100 / 150 lb | 15 / 02 / 100 / 150 lb |
| Pressure Guage | 15 / 01 / 100 / 150 lb | 15 / 01 / 100 / 150 lb | 15 / 01 / 100 / 150 lb |