ANNEXURE-I	:	TECHNICAL DATA SHEET

A – SITE CONDITION

Barometric Pressure  ……    736 mmHg.

B – TECHNICAL DATASHEET FOR EXPANSION JOINT -

| 1) |  | Medium handled | Flue Gas – Analysis ( % by Volume, wet) : CO2 – 9.9 ; O2 – 6.08 ; N2-66.69 ; Moisture – 17.33 (Saturated).;; Flue Gas with dust concentration of 60 mg/Nm3 and SOx level- 1246 mg/Nm3 (wet basis) |
| --- | --- | --- | --- |
| 1a) |  |  | Flue gas shall be saturated with 10% H2SO4 SOLUTION. |
| 2) |  | Purpose of Expansion Joint | To accommodate various thermal movement and vibration |
| 3) |  | Expansion Joint Location | At the exit of FGTR (Entry to Wet Stack) |
| 4) |  | Size | 4.8 mtr diameter duct location |
| 4a) |  | Quantity | 1 No. |
| 4b) |  | Type of Expansion Joint | Non-Metallic Type |
| 5) |  | NMEJ depth | Bidder to indicate |
| 6) |  | Operating Temp at inlet , Deg C | 53 |
| 7) |  | Operating Pressure at inlet, mmwc | 50 - 70 |
| 8) |  | Flow, Nm3/hr | 4,01,991 |
| 9) |  | Flue Gas density, kg/Nm3 | 1.254 |
| 10) |  | Axial Movement, mm | 100 (min.) Max value Bidder to indicate |
| 11) |  | Lateral movement , mm | 50 (min.) Max value Bidder to indicate |

C - MATERIAL OF CONSTRUCTION:

| Description | Material |
| --- | --- |
| Body Flange | SS 317 LMN |
| Material- Element | Bidder to indicate on the basis of flue gas parameters and acidic atmosphere as indicated. |
| Counterfanges | Carbon Steel |
| Nuts & Bolts | Carbon Steel |
| Gasket | Bidder to indicate |