## Sheet1
B&V Project No:
Owner: Hindalco Industries Limited (HIL); Consultant: Black & Veatch (B&V)
Project Name: HIL RENUSAGAR - 1 X 75kW FGD Project
Drawing No: |  | S21001-TS01-05HSC-227202 R1
Drawing Revision No: |  | 1
Drawing Title: |  | Booster Fan Specification
| HIL & BV's Comments dt. 14.01.22 | SL's Response dt.15.01.22
HIL Civil-
1 | All dimensions are not given. */** put in dimensions | These are Supplier’s data based on Suplier's design & selection of Fan. We have requested this data from the suppliers to take care of it when General Arrangement (GA) drawing of Fan will be made
2 | In the GA drawing, the elevation of the booster fan is not given. If the elevation of the buster fan is above 600 mm from ground level then consider the proper platform with railings surrounding the booster fan, access to reach the platform for the safe maintenance and operation of the booster fan. | Elevation of Booster Fan shall be obtained from the supplier of Fan. After receipt of same from the selected supplier, requirements of platform etc as desired shall be shown in the final GA drawing ( Plan and elevation) of Fan.
3 | Duct supporting arrangement not shown in the drawings. | This is the specification of Booster Fan. Support arrangement of duct etc will be shown when the duct layout drawing will be prepared.
4 | Space required around the booster fan not mentioned for future maintenance purposes for placement of crane etc.- | Same shall be shown when the GA drawing of Booster fan and also plot plan will be complete after receipt of Dimensional GA drawing of Booster Fan from the supplier.
5 | Electrical Cable Cut-outs and cable location not shown in the GA Drawing. | Please note that it is not the GA drawing of Booster Fan. The drawing /sketch attached to show them our requirement of (1) the orientation of fan (2) Duct orientation and size to select suction and discharge accordingly (3) furnishing of few important dimension enabling us to proceed for a preliminary GA drawing of booster fan even if the GA of fan is not included in the offer stage by the supplier. When the Layout and GA drawing of Booster Fan will be made , cable cut out/location shall be shown.
HIL Electrical-
Annexure - III
1 | All motor measurements such as current, temperature, bearing temperature, winding temperature cold air and hot air temperature should have Analog monitoring for booster fan motor. | Aanalogue meters are very uncommon ; however, as desired by you we will provide Analogue Meter for current measurement and be placed in the VFD panel
2 | Since there is no DC motor and HT motor in the system so remove their attribute from the sheet like 3.02.00. | Noted and removed.
3 | No comment
4 | We will prefer VPI technology in motor for Booster fan motor. | Noted and included in the revised specification
5 | Design basis for ambient temperature is not mentioned. It should be 50 DegC. | Noted and included in the revised specification
6 | Core should be of low loss silicon steel. | Noted and included in the revised specification
7 | DC supply will be 135 VDC instead of 220 VDC.As Renusagar has 135 VDC supply from battery bank #5. | Noted and changed in the revised specification.
8 | Since there is no motor above 1000KW so remove 4.14.05. | Noted . Clause removed in the revised specification
9 | We will prefer CACA and TEFC cooled motor. Hence remove the specs about water cooled motor.- | Noted. Specification of water cooled motor is removed
10 | Technical specs applicable to booster fan motor should be in this sheet. removed all irrelevant and generalised statements. | Noted
11 | VFD should have the Input voltage rating 690 V instead of 6.6 KV. - | Noted and incorporated in the revised specification
| List of Preferred MAKE: | Shall be included in revised Spec.
| ITEMS | Make
1 | Bearings | SKF
2 | RTD | Pyroelectric/ Waaree
3 | Pneumatic Actuator. | Kelton.
4 | MOTOR | BHEL/ ABB/ Siemens
5 | VFD | ABB/ Siemens/Amteck
6
7