|  |  | Owner: HINDALCO INDUSTRIES LIMITED Ahura Centre, 1st Floor, B Wing, Mahakali Caves Road, Andheri (East), Mumbai - 400 093, India |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | EPCM Contractor: W. L. GORE & ASSOCIATES (Pacific) Pte, Ltd. India Branch 703, A-Wing, 215 Atrium, Andheri Kurla Road, Mumbai 400059, India |  |  |  |  |  |
|  |  | Nominated Subcontractor - Engineering, Quality Control, Supervision: SMARTLuth Solution and Service Pvt. Ltd. Unit No: 503, 5th Floor, ECO Centre,. EM-4 Sector-V, Salt Lake City, Kolkata - 700091, India |  |  |  |  |  |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System DESIGN BASIS REPORT - Mechanical DESIGN BASIS REPORT - Mechanical ` ) ) ISSUED FOR; APPROVAL; INFORMATION; MANUFACTURING; CONSTRUCTION; AS-BUILT. |
| 0a | 21.02.2022 | First Submission | IR |  | IR |  | BCB |
| 00 | 14.02.2022 | First Submission | IR |  | IR |  | BCB |
| Rev. | Date | Description of revision | Prepared | Checked |  |  | Approved |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant |  |  | Drg. / Doc. No.: S21001-TS01-05HSC-XXXXXX |  |  |  |  |
| Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System |  |  | Gore Doc. No.: RPDU5.PA.XXX |  |  | page 1 of 4 |  |
| Design Basis Report - Mechanical |  |  | GORE Job No.: RPDU5 |  |  | Rev. : 0a |  |
|  |  |  | File: Tech Spec of Booster Fan |  |  |  |  |
| This document is a property of W.L. GORE & ASSOCIATES (Pacific) Pte, Ltd. and it may contain trade secrets or privileged, undisclosed or otherwise confidential information. If you have received this document in error, you are hereby notified that any review, copying or distribution of it is strictly prohibited. |  |  |  |  |  |  |  |

`

Hindalco Industries Ltd.

Renusagar Unit No. 5 FGD System

Design Basis Report – Mechanical

1.00.00 	System Description

Hindalco Industries Ltd (HIL) is going to install a Flue Gas Desulphurization (FGD) system for 1X 80MW coal fired unit no. 5 at Renusagar, UP. The system is based on technology and equipment provided by W. L. Gore & Associates Inc (WLG) based on their proprietary catalytic exchange system.

The basic process is shown in the Process Flow Diagram (Drawing No. S21001-XF01-05HSD-227001) attached with this design basis report (DBR). The flue gas is tapped downstream of the main plant ID fans discharge duct before the existing stack and led to the new system with a Booster Fan. The system consists of a Mist Cooling Unit (MCU) followed by the Flue Gas Treatment Reactor (FGTR), where the sulfur is removed in presence of catalyst modules. The clean flue gas is led to a bypass stack placed above FGTR structure. FGTR houses a mist eliminator before discharging to chimney. The proper performance of the catalyst for sulfur exchange requires that the flue gas temperature reaching it should be not more than 53-540C and the gas should be 100% saturated. MCU is provided ahead of the FGTR to meet this requirement. Apart from misting in the MCU, FGTR is also provided with additional misting & washing nozzles to operate in a pre-selected sequence for the best performance of the catalyst at all times.

Fresh water (Filter water quality) is provided from the existing plant water system for this purpose of saturation of flue gas. However, a substantial portion of water will be re-used after filtration, as necessary, in the system to limit make-up water requirement to the minimum. Sulfur on removal from flue gas combines with water to form dilute sulfuric acid (~10%). The dilute acid is taken to an Acid Concentrating Plant (ACP) where the acid is concentrated with the help of steam and will be available as a byproduct for commercial use. The dust laden wash water – not reusable in the system – will be sent to existing plant drainage system. The plant water balance is shown in the attached mass balance diagram (Drawing No. S21001-XF01-05HSD-227001 (CALC))

The system will be provided with proper instrumentation & control for monitoring and semi-automatic operation from a PLC with proper safety interlocks.

As shown in the PFD, the major equipment, apart from FGTR & MCU, involved in the system are a) booster fan, b) various pumps for water & acid services, c) miscellaneous tanks for water and acid services, d) valves, piping & specialties connecting the equipment and d) flue gas ducting & dampers. Variable Frequency Drive (VFD) will be provided for booster fan for capacity adjustment matching the main plant operation.

2.00.00 	Standards

The system will be designed to conform to all statutory requirements – particularly on environment, health & safety as applicable to the plant.

All equipment, piping & materials except proprietary items supplied by WLG, shall be procured as per the latest applicable standard of BIS or its appropriate equivalent.

The materials of construction shall be selected for various services with proper considerations for protection against corrosion and erosion.

3.00.00 	Major Design Considerations

3.01.00 	Sizing Criteria

A margin of 10 - 15% on capacity has been considered on the calculated requirement for the various pumps and fan. However, while calculating required head, no additional margin will be provided to avoid oversizing.

The booster fan carries a margin of 10% on volume & 19% on head.

Drive motors shall be selected with 15% margin on rated power requirement. Pumps operating in parallel will be designed to operate within the safe operating zone of the system head-capacity curve.

The atmospheric tanks shall have minimum 10% free capacity over the highest liquid level. The storage capacity shall be selected considering uninterrupted safe operation without inflow. The separate gravity assisted water spraying system provided for catalyst protection in FGTR capacity will be sufficient to safeguard the system for 10 minutes.

The following velocity guidelines shall, in general, be followed for sizing of pipes and ducting:

- Water/Acid Lines

Pump Discharge: 1.8 – 2.5 m/s

Pump Suction:     1-1.5m/s

- Flue Duct:	12 – 14m/s

Design pressure and temperature of the pipes, valves and specialties shall be selected to the nearest standard pressure class rating considering maximum encountered within the pipe/duct. Negative pressure systems will be designed for full vacuum.

To isolate vibration & also to take some thermal expansion, inlet & outlet of the fans will have non-metallic expansion joints.

Specifically, the following aspects will be considered for flue duct design:

a) Internal design pressure for the flue casing is - 400 mmwg upto Booster fan & + 350 mmwg beyond booster fan.

b) Casing stiffeners are designed for deflection of no more than L/360.

c) A dust layer of 150 mm height having a density of 1000 kg/m3 has been considered.

d) All expansions will be calculated with gas temperature of 155 DegC upto MCU & 80 DegC beyond MCU.

e) Non-metallic expansion joints will be designed for axial movement of calculated movement + 25 mm & calculated movement +/- 15 mm for lateral movement.

f) Quick closing pneumatic seal type dampers are provided after tap off from existing flues. New dampers will also be provided in existing flue line to Chimney after tap-off.

3.02.00 	Equipment Type

- Water service pumps	Horizontal centrifugal

- Drain pumps	Vertical non-clog pump

- Acid handling pumps	Horizontal centrifugal/positive displacement

- Booster fan	Radial double inlet; simply supported type, 	backward curved vanes, provided with both 	damper & VFD control

- MCU	Approx. 8 m wide x 4 m deep. The desired	flue gas temperature after MCU is 54 DegC.	The casing will be designed in parity with flue	duct. For structural loading, hoppers below	will be considered to be full of water. For		thermal expansion calculation, a gas		 temperature of 100 DegC considered below	spray nozzle elevation

- FGTR	The catalyst layers are arranged in 15x11		boxes in plan. There are several levels. Each	level houses 5 layers of catalyst, one placed	on top of the other.designed for future 	emission consideration (200 mg/Nm3 dry at	6% oxygen) and also houses one level for		catalyst management. However, internals	for future situation has not been provided 	now. Hoppers below FGTR will be considered 	to be full of acid	water having a density of 	1100 kg/m3.					The live loads for the module loading and	unloading gallery has been suitably taken to 	allow 3 level stacking. The casing will be 	designed in parity with flue duct.

- Chimney 	10m tall with bottom diameter of 4800 mm	and a top diameter of 3200 mm. The flue is 	discharged through a SS 317 LMN cone 	having a 	diameter of 2800 mm (exit velocity 	through	the cone is 22 m/s). The Chimney

will be made from MS plate of required thickness and will be lined with glass flakes on the inside and painted with suitable paints on the outside.

3.03.00 	Materials of Construction

The salient materials of construction are as follows:

- Ducts/hoppers & FGTR Enclosure	CS with anti-corrosive Glass flake 	lining / paint

- Fan blades	Provided with liners & or weld 	overlays for long life

- FGTR	Load carrying beams SS grade		S317LNM; Casing 6 thk MS	plate; lined with Glass flakes 2.0 mm 	thk

- MCU	6 thk MS plate; lined with Glass

flakes	2.0 mm thk

- Chimney	MS plate of required thk; lined with	Glass flakes and painted with

suitable 	paints on the outside

- Low pressure pipelines & valves	PVC/CPVC/CS

- Pipes for corrosive fluids	SS/PVC/CPVC

- Pumps	SS/PVC

- Spray Nozzles	PVDF

3.04.00 	Layout Considerations

The new system is being installed in an old, existing power plant within a constrained area adjacent to the existing ID ducting leading to chimney. Sufficient care is being taken in placing equipment without disturbing the existing structures and facilities. However, the layout has been developed considering the ease of erection and subsequent maintenance of installed equipment.

For FGTR, each level has been provided with all around gallery except for gas entry level. Access door is provided on FGTR casing for handling of catalyst modules. Each level has 2 nos large access doors & 2 nos inspection doors. Each level has an array of washing nozzles and an array of misting nozzles. Minimum width of walkway on platforms has been provided as 1m. A large gallery of 2500 mm width has been provided in front of access doors to facilitate module insertion and storage. Two staircases have been provided on the FGTR structure for access to platforms at different levels.

The sampling point for CEMS will be located at the base of the chimney. Adequate gallery has been provided at this level. This level is accessible through staircase from both sides. The Chimney will be provided with aviation light

Monorail hoist of SWL of 1.0 MT has been considered for lifting & lowering of catalyst modules up to top level at FGTR from ground. The FGTR gallery will have a designated cavity for lifting modules. Similar handling facility will be provided for booster fan and drive.

Suitable paving and approach road from the existing plant road is envisaged for access to major structures.

The control system will be installed on a floor to be constructed above the existing electrical building near the FGTR.