## comparison
TECHNICAL EVALUATION OF OFFER OF NOZZLES
SR.NO | DESCRIPTION | SPECIFICATION REQUIREMENT | LECHLER | SPRAYTECH | EVALUATION REMARK
A | WASH NOZZLE
1 | FLOW RATE | 11 LPM | 11 LPM | 11 (+/-)10% LPM | 1. Both companies meet the nozzle quantity , flow and pressure and specification. 2. However, spraytech is to indicate the orifice size. 3. Regarding MOC, PP material is chemically better than PVDF quoted by Lechler.
2 | PRESSURE | 1.5 BAR G | 1.5 BAR G | 1.5 BAR G
3 | SPRAY ANGLE | 90 DEG | 90 DEG | 90(+/-) 5 DEG
4 | MOC | PP/CPVC | PVDF | PP
5 | NARROWEST CROSS SECTION | BY BIDDER | 3.2 MM | NA
6 | CONNECTION SIZE | NOT SPECIFIED | 3/8 INCH BSPT | 3/8 INCH BSP(M)
7 | QUANTITY | 990 NOS | 990 NOS | 990 NOS
8 | MODEL NO | BY BIDDER | 460.846.5E.CE.00.0 | DA26.125.P2.XC
B | MISTING NOZZLE
1 | FLOW RATE | 2/2.35 LPM | 2.42 LPM | 2.416 LPM | 1.Spraytech meets the required capacity thru nozzle as desired with a pressure less than the aexpected pressure specified.. 2. Lechler does not meet the capacity even at higher pressure. 3. Spraytech requires to provide the orifice size 4.Regarding MOC, PP material is chemically better than PVDF quoted by Lechler.
2 | PRESSURE | 2 BARG | 2/3 BAR G | 1.5 BAR G
3 | SPRAY ANGLE | 90 DEG | 90 DEG | 90(+/-) 5 DEG
4 | MOC | PP/CPVC | PVDF | PP
5 | NARROWEST CROSS SECTION | BY BIDDER | 1.3 MM | NA
6 | CONNECTION SIZE | NOT SPECIFIED | 1/8 INCH BSPT | 1/4 INCH BSP(M)
7 | QUANTITY | 440 NOS | 440 NOS | 440 NOS
8 | MODEL NO | BY BIDDER | 460.526.5E.CA.00.0 | BG16.250.P2.XB
C | MAKE UP WATER NOZZLES
1 | FLOW RATE | TOTAL 27.17 LPM | 0.42 LPM | 0.7 LPM | Both the Bidders are to resize their nozzles's capacity and to select the proper model considering that the nos of nozzles requirement is 9 (Or 18) only having total flow capacity 1.63 m3/hr (27.2 LPM)
2 | PRESSURE | BY BIDDER | 1 BAR G | 1 BARG
3 | SPRAY ANGLE | BY BIDDER | 120 DEG | 60(+/-) 5 DEG
4 | MOC | PP/CPVC | PVDF | PVDF
5 | NARROWEST CROSS SECTION | BY BIDDER | 0.2 MM | NA
6 | CONNECTION SIZE | NOT SPECIFIED | 1/8 INCH BSPT (M) | 1/8 INCH BSPT
7 | QUANTITY | NOT SPECIFIED | 64 NOS | 80 NOS
8 | MODEL NO | BY BIDDER | 460.368.5E.CA.00.0 | DA14.100.P6.YA

## Lechler
TECHNICAL EVALUATION OF OFFER OF NOZZLES
SR.NO | DESCRIPTION | SPECIFICATION REQUIREMENT | LECHLER | EVALUATION REMARK
A | WASH NOZZLE
1 | FLOW RATE | 11 LPM | 11 LPM | 1. Lechler meets the nozzle quantity , flow and pressure and specification. 2. Regarding MOC, PVDF quoted by Lechler is not as good as PP so far resistance to chemical is concered.
2 | PRESSURE | 1.5 BAR G | 1.5 BAR G
3 | SPRAY ANGLE | 90 DEG | 90 DEG
4 | MOC | PP/CPVC | PVDF
5 | NARROWEST CROSS SECTION | BY BIDDER | 3.2 MM
6 | CONNECTION SIZE | NOT SPECIFIED | 3/8 INCH BSPT
7 | QUANTITY | 990 NOS | 990 NOS
8 | MODEL NO | BY BIDDER | NA
B | MISTING NOZZLE
1 | FLOW RATE | 2/2.35 LPM | 2.42 LPM | 1. Lechler does not meet the capacity even at higher pressure. 2.Regarding MOC, PP material is better than PVDF quoted by Lechler
2 | PRESSURE | 2 BARG | 2/3 BAR G
3 | SPRAY ANGLE | 90 DEG | 90 DEG
4 | MOC | PP/CPVC | PVDF
5 | NARROWEST CROSS SECTION | BY BIDDER | 1.3 MM
6 | CONNECTION SIZE | NOT SPECIFIED | 1/8 INCH BSPT
7 | QUANTITY | 440 NOS | 440 NOS
8 | MODEL NO | BY BIDDER | NA
C | MAKE UP WATER NOZZLES
1 | FLOW RATE | TOTAL 27.17 LPM | 0.42 LPM | Lechler is to resize their nozzles's capacity and to select the proper model considering that the nos of nozzles requirement is 9 (Or 18) only having total flow capacity 1.63 m3/hr (27.2 LPM)
2 | PRESSURE | BY BIDDER | 1 BAR G
3 | SPRAY ANGLE | BY BIDDER | 120 DEG
4 | MOC | PP/CPVC | PVDF
5 | NARROWEST CROSS SECTION | BY BIDDER | 0.2 MM
6 | CONNECTION SIZE | NOT SPECIFIED | 1/8 INCH BSPT (M)
7 | QUANTITY | NOT SPECIFIED | 64 NOS
8 | MODEL NO | BY BIDDER | NA

## Spraytech
TECHNICAL EVALUATION OF OFFER OF NOZZLES
SR.NO | DESCRIPTION | SPECIFICATION REQUIREMENT | SPRAYTECH | EVALUATION REMARK
A | WASH NOZZLE
1 | FLOW RATE | 11 LPM | 11 (+/-)10% LPM | 1. Spraytech meets the nozzle quantity , flow and pressure and specification. 2. However, spraytech is to indicate the orifice size. 3. Regarding MOC, PP material is better than PVDF quoted by Lechler.
2 | PRESSURE | 1.5 BAR G | 1.5 BAR G
3 | SPRAY ANGLE | 90 DEG | 90(+/-) 5 DEG
4 | MOC | PP/CPVC | PP
5 | NARROWEST CROSS SECTION | BY BIDDER | NA
6 | CONNECTION SIZE | NOT SPECIFIED | 3/8 INCH BSP(M)
7 | QUANTITY | 990 NOS | 990 NOS
8 | MODEL NO | BY BIDDER | DA26.125.P2.XC
B | MISTING NOZZLE
1 | FLOW RATE | 2/2.35 LPM | 2.416 LPM | 1.Spraytech meets the required capacity thru nozzle as desired with a pressure less than the aexpected pressure specified.. 2. Syntech requires to provide the orifice size 3.Regarding MOC, PP material is better than PVDF quoted by Lechler
2 | PRESSURE | 2 BARG | 1.5 BAR G
3 | SPRAY ANGLE | 90 DEG | 90(+/-) 5 DEG
4 | MOC | PP/CPVC | PP
5 | NARROWEST CROSS SECTION | BY BIDDER | NA
6 | CONNECTION SIZE | NOT SPECIFIED | 1/4 INCH BSP(M)
7 | QUANTITY | 440 NOS | 440 NOS
8 | MODEL NO | BY BIDDER | BG16.250.P2.XB
C | MAKE UP WATER NOZZLES
1 | FLOW RATE | TOTAL 27.17 LPM | 0.7 LPM | Spraytech is to resize their nozzles's capacity and to select the proper model considering that the nos of nozzles requirement is 9 (Or 18) only having total flow capacity 1.63 m3/hr (27.2 LPM)
2 | PRESSURE | BY BIDDER | 1 BARG
3 | SPRAY ANGLE | BY BIDDER | 60(+/-) 5 DEG
4 | MOC | PP/CPVC | PVDF
5 | NARROWEST CROSS SECTION | BY BIDDER | NA
6 | CONNECTION SIZE | NOT SPECIFIED | 1/8 INCH BSPT
7 | QUANTITY | NOT SPECIFIED | 80 NOS
8 | MODEL NO | BY BIDDER | DA14.100.P6.YA