## Sheet1
ANNEXURE-1
PROCESS PUMPS DATA SHEET
Item No. | 1
Description of the Pumps | PROCESS WATER PUMP
Design Standard | Relevant IS/API/BS/ASME/ANSI/ ASTM standard and Hydraulic Institute Standard
Testing Standard | HIS (Hydraulic Institute Standard)
Tag No. | PWP-1/2
LIQUID | 0.25% H2SO4 Solution plus Fresh make up of filter water quality
Operating Temp. at Deg. C. | Ambient
Solid Concentration and particle size | Nil
Specific Gravity | 1
Dynamic Viscosity, Poise | 0.0091
Qty Reqd. | 02 nos ( 1w+1s)
Pump Type | Horizontal Centrifugal pump with flooded suction
Installation | Open to Atmosphere
Rated Capacity (m3/hr) | 36
Total Dynamic Head (MWC) | 160
Head provided in MWC | Bidder to furnish
Pump Model | Bidder to furnish
Pumps Design and construction standard | IS/API/Hydraulic Institute Standard-USA / relevant ASTM/ISO/BS standard
Casing | SS-316L(CF8M)
Shaft | SS-316L
Shaft Sleeve | Bidder to furnish
Impeller | SS-316L
Bearing and Bearing housing | Bidder to furnish
Sealing | Mechanical Sealing- Bidder to indicate material of seal.
Size (Suc x Del) mm NB | Bidder to furnish
Efficiency | Bidder to furnish
BKW | Bidder to furnish
Motor KW rating | Bidder to furnish
RPM | Bidder to furnish
Motor Make | Siemens/ABB/Equivalent
Motor Data Sheet | Bidder to furnish
NPSHR in MWC | Bidder to furnish
Performance Curve Capacity vs. Head, NPSHR, Power and Efficiency | Bidder to furnish
Counterflanges | Bidder shall supply all inlet and outlet counterflanges, with nuts , bolts and gaskets as per ANSI B 16.5 and material as per pump material.
Drive Motor | As per separate annexure of standard spec of electric motors
Protection | Suitable as per outdoor installation location of the pump as stated above
Accessories | Flexible coupling with guard, common steel base plate /structural frame for pump and its drive, Fixation Nuts and Bolts with the foundation
General Requirement | Equipment shall be properly epoxy painted against Sulphate environment. Pumps shall have rising head-capacity characteristic and suitable for parallel operation. Operating range of pumps shall be 30% to 130% of rated flow as minimum. Minimum flow thru’ the Pumps shall be 30% or less of rated flow
Testing Requirement | Performance testing of Pumps,NDT for Impeller, shaft and casing. Bidder to consider DP test for impeller and casing and UT for Shaft as minimum. Hydraulic Test shall be as per Hydraulic Institute Standard at a pressure of 150 % of shut off head of pump for 1 hour. Dynamic balancing test as per relevant ISO standard for Shaft and Impeller.
Guarantee Data which will attract penalty for non-fulfilment | 1. Specified Rated Capacity and Head of Pump.
2. Pump Efficiency at the duty point
3. Power Requirement at the motor terminal at the rated point operation of pump.