## Sheet1
ANNEXURE-1
PROCESS PUMPS DATA SHEET
Item No. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Description of the Pumps | FRESH WATER PUMP | PUMP TO CLIENT SERVICES | MODULE WASH PUMP | FGTR EFFLUENT TRANSFER PUMP | SAC INLET PUMP | SAC RECOVERED WATER RETURN PUMP | 95% ACID TANKER LOADING PUMP | 95% ACID START UP RECIRCULATION PUMP
Design Standard | Relevant IS/API/BS/ASME/ANSI/ ASTM standard and Hydraulic Institute Standard
Testing Standard | HIS (Hydraulic Institute Standard)
Tag No. | FWP-1/2 | PCS-1/2 | MWP-1/2 | FETP-1/2 | SIP-1/2 | RWRP-1/2 | CALP-1/2 | CARP-1/2
LIQUID | FILTER WATER | NEUTRALISED BLOWDOWN WATER WITH SUSPENDED SOLIDS | 10% H2SO4 SOLUTION | 10% H2SO4 SOLUTION | 10% H2SO4 SOLUTION | 0.25% H2SO4 SOLUTION | 95% H2SO4 SOLUTION | 95% H2SO4 SOLUTION
Operating Temp. at Deg. C. | Ambient | 60 | 60 | 60 | 60 | 60 | 60 | 60
Solid Concentration and particle size |  | 200 PPM ; 10 - 100 MICRONS | Nil | Nil | Nil | Nil | Nil | Nil
Specific Gravity | 1 | 1 | 1.065, Bidder to confirm | 1.065, Bidder to confirm | 1.065, Bidder to confirm | 1 | 1.8, Bidder to confirm | 1.8, Bidder to confirm
Dynamic Viscosity, Poise | 0.0091 | 0.0091 | 0.11, Bidder to confirm | 0.11, Bidder to confirm | 0.11, Bidder to confirm | 0.0091 | 0.24 | 0.24
Qty Reqd. | 02 nos ( 1w+1s) | 02 nos ( 1w+1s) | 02 nos ( 1w+1s) | 02 nos ( 1w+1s) | 02 nos ( 1w+1s) | 02 nos ( 1w+1s) | 02 nos ( 1w+1s) | 02 nos ( 1w+1s)
Pump Type | Horizontal Centrifugal pump with flooded suction | Horizontal Centrifugal pump with flooded suction | Horizontal Centrifugal pump with flooded suction | Horizontal Centrifugal pump with flooded suction | Horizontal Centrifugal pump with flooded suction | Horizontal Centrifugal pump with flooded suction | Horizontal Centrifugal pump with flooded suction | Horizontal Centrifugal pump with flooded suction
Installation | Open to Atmosphere
Rated Capacity (m3/hr) | 40 | 15 | 100 | 12 | 12 | 12 | 15 | 1
Total Dynamic Head (MLC) | 65 | 35 | 70 | 50(HOLD) | 30 | 35 | 20 | 20
Head provided in MLC | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
Pump Model | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
Pumps Design and construction standard | IS/API/Hydraulic Institute Standard-USA / relevant ASTM/ISO/BS standard
Casing | FRP/PP | FRP/PP | FRP/PP | FRP/PP | FRP/PP | FRP/PP | FRP/PP | FRP/PP
Shaft | SS+Ceramic | SS+Ceramic | SS+Ceramic | SS+Ceramic | SS+Ceramic | SS+Ceramic | SS+Ceramic | SS+Ceramic
Shaft Sleeve | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
Impeller | FRP/PP | FRP/PP, Hardened | FRP/PP | FRP/PP | FRP/PP | FRP/PP | FRP/PP | FRP/PP
Bearing and Bearing housing | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
Sealing | Mechanical Sealing- Bidder to indicate material of seal. | Mechanical Sealing | Mechanical Sealing |  | Mechanical Sealing | Mechanical Sealing | Mechanical Sealing | Mechanical Sealing | Mechanical Sealing | Mechanical Sealing
Size (Suc x Del) mm NB | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
Efficiency | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
BKW | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
Motor KW rating | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
RPM | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
Motor Make | Siemens/ABB/Equivalent
Motor Data Sheet | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
NPSHR in MWC | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
Performance Curve Capacity vs. Head, NPSHR, Power and Efficiency | Bidder to furnish | Bidder to furnish | Bidder to furnish |  | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish | Bidder to furnish
Counterflanges | Bidder shall supply all inlet and outlet counterflanges, with nuts , bolts and gaskets as per ANSI B 16.5 and material as per pump material.
Drive Motor | TEFC, Induction type, class F insulation but with temperature rise limited to that of class B, 415 V, 3-phase, 50 Hz, motor rating shall be 10% more than the maximum pump power requirement and be sized as per next higher frame size. Where DC Motor is mentioned, it shall be provided as per spec.
Protection | Suitable as per outdoor installation location of the pump as stated above
Accessories | Flexible coupling with guard, common steel base plate /structural frame for pump and its drive, Fixation Nuts and Bolts with the foundation
General Requirement | Equipment shall be properly epoxy painted against Sulphate environment. Pumps shall have rising head-capacity characteristic and suitable for parallel operation. Operating range of pumps shall be 30% to 130% of rated flow as minimum. Minimum flow thru’ the Pumps shall be 30% or less of rated flow
Testing Requirement | Performance testing of Pumps,NDT for Impeller, shaft and casing. Bidder to consider DP test for impeller and casing and UT for Shaft as minimum. Hydraulic Test shall be as per Hydraulic Institute Standard at a pressure of 150 % of shut off head of pump for 1 hour. Dynamic balancing test as per relevant ISO standard for Shaft and Impeller.
Guarantee Data which will attract penalty for non-fulfilment | 1. Specified Rated Capacity and Head of Pump.
2. Pump Efficiency at the duty point
3. Power Requirement at the motor terminal at the rated point operation of pump.