|  |  | Owner: HINDALCO INDUSTRIES LIMITED Ahura Centre, 1st Floor, B Wing, Mahakali Caves Road, Andheri (East), Mumbai - 400 093, India |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | EPCM Contractor: W. L. GORE & ASSOCIATES (Pacific) Pte, Ltd. India Branch 703, A-Wing, 215 Atrium, Andheri Kurla Road, Mumbai 400059, India |  |  |  |  |  |
|  |  | Nominated Subcontractor - Engineering, Quality Control, Supervision: SMARTLuth Solution and Service Pvt. Ltd. Unit No: 503, 5th Floor, ECO Centre,. EM-4 Sector-V, Salt Lake City, Kolkata - 700091, India |  |  |  |  |  |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System Kraftwerk-Kennzeichen-System Identification System PRELIMINARY NOT VALID FOR CONSTRUCTION ISSUED FOR; APPROVAL; INFORMATION; MANUFACTURING; CONSTRUCTION; AS-BUILT. |
| 02 | 10/12/2021 | Media Specification included | S.DAS | S. Chakraborty |  |  | M.DEB |
| 01 | 19/11/2021 | General Revision | S.DAS | S. Chakraborty |  |  | M.DEB |
| 00 | 17/11/2021 | Initial Release | S.DAS | S. Chakraborty |  |  | M.DEB |
| Rev. | Date | Description of revision | Prepared | Checked |  |  | Approved |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant |  |  | Drg. / Doc. No.: S21001-PM01-05CPP-121004 |  |  |  |  |
| Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System |  |  | Gore Doc. No.: RPDU5.MP.500 |  |  | page 1 of 30 |  |
| Kraftwerk-Kennzeichen-System Identification System |  |  | GORE Job No.: RPDU5 |  |  | Rev. : 02 |  |
|  |  |  | File: KKS Identification System R2 |  |  |  |  |
| This document is a property of W.L. GORE & ASSOCIATES (Pacific) Pte, Ltd. and it may contain trade secrets or privileged, undisclosed or otherwise confidential information. If you have received this document in error, you are hereby notified that any review, copying or distribution of it is strictly prohibited. |  |  |  |  |  |  |  |

Project Name: 	Flue Gas Desulphurization Equipment with GORETM SPC Technology

Project No: 				 	          S21001

Documentation Numbering Procedure: 	VGB KKS System

Purpose: 	This document outlines the procedure for tagging Equipment, Specialty Items, Valves, Pipelines & Instrument systems. This procedure serves to control the identification of systems and components by using the Kraftwerk-Kennzeichen-System Identification System, hereafter referred to as KKS tagging system.

This system provides a means to identify plant facilities, equipment, piping, or any other plant components as defined within the attachments to this procedure.

The fields that make up for an equipment tag are:

- Plant Code

- System Code

- System Numbering

- Device Type Code

- Device Number

- Component Code

The identification codes to be used and the associated text explanations are specified within this KKS Tagging Procedure. Should it become necessary to add or modify certain identification codes in the course of the project, same shall be done.

Gaps in the Device Number for each combination of Unit Code, System Code, System Numbering Code, Device Type Code, and Component Code are acceptable, but shall be avoided, in general. The sequential increment of numbers used as tag number shall be from south to north and from west to east and from the lower elevations to higher elevations.

General format of drawing/document number:

- SXXYYY: 	Project Number has been identified with S21001.

- ZZNN:		Document type code of FGD system: (Document Type)

- EN01= Engineering Documents and Drawings.

- QA01= QA Documents.

- QC01= Quality Control Document.

- IP01= Inspection Test Plan.

- PS01= Erection Procedure/Work Method Statement.

- MA01= Manual/ OPERATING/ GENERAL

- XF01= PFD Diagram.

- XG01= P& I Diagram.

- TS01= Technical Specification.

- MS01= Master Project Schedule.

- CS01= Cable Schedule.

- VS01= Valve Schedule

- PM01= Project management

- IT01= information technology/Software

- EE01= Engineering Issues

- CC01= Commissioning Procedure

- AA:			Discipline Codes as below

        - 11: General/PM/Communications

        - 22: Mechanical

        - 33: Electrical

        - 44: Control & Instrumentation

        - 55: Civil & Structures

        - 66: QA/QC

        - 77: HSE/EHS

        - 88: IT/ SOFTWARES

        - 99: SAC (TO BE UPDATED LATER)

- NNNN:			Serial Numbers as (XLS file)

        - Pre-defined

PLANT TAGGING, KKS-CODING PHILOSOPHY

| Serial No. of breakdown | 0 |  |  | 1 |  |  |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Name of breakdown | Total Plant |  |  | System Code/Function |  |  |  |  |  |  | Equipment Unit Code |  |  |  |  | Component Code |  |  |  |
| Designation of Data Character | G |  |  | F0 |  | F1F2F3 |  | FN |  |  | A1A2 |  | AN |  |  | B1B2 |  | BN |  |
| Type of Data Character | ('A' OR 'N') |  |  | NN |  | AAA |  | NN |  |  | AA |  | NNN |  |  | AA |  | NN |  |
| Identification of power station units and unit independent plants |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Plant Code |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| System-classifying Classifying sub-division of system and plants of unit (As per KKS Code table) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Numbering subdivision of system and plants into sub-systems in systematic manner |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Classification of equipment as per KKS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Numbering of equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Classification of components as per KKS key |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Numbering of components, signals or signal applications |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

VGB KKS CODES

| Function Key, Main Groups as per KKS code |  |
| --- | --- |
| A | Grid and distribution system |
| B | Power transmission and auxiliary power supply |
| C | Instrumentation and control equipment |
| D | Not Used |
| E | Fuel supply and residues disposal |
| F | Handling of nuclear equipment |
| G | Water supply and disposal |
| H | Heat generation |
| J | Nuclear heat generation |
| K | Reactor auxiliary system |
| L | Steam, water, gas cycle |
| M | Main machine set |
| N | Process energy/fluid supply for external users (e.g., district heating) |
| P | Cooling water system |
| Q | Auxiliary system |
| R | Gas generation and treatment |
| S | Ancillary system |
| T | Not Used |
| U | Structure |
| V | Civil work and Construction work |
| W | Renewable energy plant |
| X | Heavy machinery (not main machine sets) (e.g., emergency diesel and generator sets) |
| Y | Not Used |
| Z | Workshop and office equipment |

KKS SYSTEM OR FUNCTION CODES (TABLE: 1)

Rev-2

| SL No | KKS Codes | KKS SYSTEM/ FUNCTION DESCRIPTION |
| --- | --- | --- |
| 1 | HTH | Mist cooling Unit (MCU) |
| 2 | HSD | Flue Gas Treatment Reactor (FGTR) |
| 3 | HTA | Flue Gas Ducting System |
| 4 | HNE | Wet Stack System |
| 5 | HSF | Mist Eliminator |
| 6 | HSC | Booster Fan System |
| 7 | HSM | 10% Acid Concentration Process water system from FGTR |
| 8 | GNK | 1% Acid Concentration Process water system from MCU |
| 9 | HTD | Sprinkler/Scrubbing/Spray System in FGTR |
| 10 | HSQ | Sprinkler/Scrubbing/Spray System in MCU |
| 11 | PBL | Fresh water System |
| 12 | LBG | HP & MP Steam Saturated |
| 13 | LCN | HP & MP Condensate |
| 14 | PAR | Make -up water System |
| 15 | GCN | Chemical Supply final product 95% concentrated Sulfuric acid |
| 16 | GNE | Sulfuric acid plant |
| 17 | SGA | Fire Fighting System |

System Numbering (FN)

System Numbering is numbering subdivision of systems and plants into subsystems and sections of plants. It forms the second part of System code. Numbering starts a new when one of the preceding code elements changes.

Following rules must be applied to the system numbering in ‘FN’:

In process-related identification the direction of flow takes priority over local conventions for orientation.

FN numbering is governed by the following principles:

- Numbering starts a new when one of the preceding code elements changes.

- Numbering is grouping (e.g.,10, 20, 30… or 01, 02, 03…………).

- Redundant zeros must be written.

- Numbering need not be continuous (i.e., sequence of 05, 10, 17, 55, etc. shall be acceptable).

- The direction of numbering coincides as a rule with that of fluid flow.

- Numbering conventions, once established, may not be altered, not even in the event of changes made in the progress of planning

KKS Equipment Unit Code (Examples):

Few General defined Examples of Equipment Unit Classification Code (A1A2)

| A | Mechanical Equipment |
| --- | --- |
| AA | Valves, Dampers, etc. incl., actuators; AISO Manual |
| AB | Isolating elements, air locks |
| AC | Heat exchangers |
| AE | Turning, driving, lifting and slewing gear (incl. manipulators) |
| B | Mechanical Equipment |
| BB | Vessels, storage equipment’s (tanks) |
| BE | Shafts (for erection and maintenance only) |
| BF | Foundations |
| BG | Boiler heating surfaces |
| BN | Jet pumps, ejectors, injectors |
| BP | Flow restrictors and limiters (incl. rupture discs), orifices (not metering orifices) |
| BQ | Hangers, supports, frames, racks, pipe penetrations |
| BR | Piping, ductwork, chutes |
| C | Direct Measuring Circuits |
| CD | Density |
| CE | Electrical variables |
| CF | Flow, rate |
| CG | Distance, length, position, direction of rotation |
| CK | Time |
| CL | Level (also for dividing line) |
| CM | Moisture, humidity |
| CP | Pressure, Differential Pressure |
| CQ | Quality variables (analysis, pH, material properties) other than *CD*, *CM*, *CV* |
| CR | Radiation variables |
| CS | Velocity, speed, frequency(mechanical) |
| CT | Temperature |
| CU | Combined variables |
| CV | Viscosity |
| CW | Weight, mass |
| CX | Neutron flux (reactor power) |
| CY | Vibration, expansion, acceleration |
| G | Electrical & Instrumentation Equipment |
| GA | Analog Junction boxes |
| GB | Binary Junction boxes |
| GC | RTD Junction boxes |

Equipment Unit Numbering (AN)

Equipment unit numbering is numbering of the mechanical, electrical and control and instrumentation equipment and forms the second part of Equipment unit code.

Equipment numbering will be single stepped as 001, 002, …, 999 and according to numbering of piping, valve and measuring circuit.

- See Table 2 for numbering of valves

- See Table 3 for numbering of Instruments.

| Table 2 (Numbering of Valves) |  |  |
| --- | --- | --- |
| Sequence / Range From | Sequence / Range up to | Type of valve |
| 1 | 99 | Motorized Actuated on-off Valves |
| 100 | 299 | Pneumatic Actuated on-off Valves |
| 300 | 399 | Control Valves |
| 400 | 499 | Safety Valves |
| 500 | 599 | Check Valves |
| 600 | 999 | Manual Valves |

| Table 3 (Numbering of Instruments) |  |
| --- | --- |
| Sequential Number Range | Measuring Circuits |
| 001 – 099 | Primary Elements i.e., FE, AE, TE, VE, WE |
| 101 – 199 | Process Transmitters i.e., DT, FT, LT, PT, AT, ST, TT, WT, VT, pHT, DPT |
| 201 – 299 | Process Switches (Blind) i.e., FS, LS, PS, TS, VS, DPS |
| 301 – 399 | Not Used |
| 401 – 499 | Test Measurements i.e., PP, TW |
| 501 – 699 | Local Indicators / Gauges / Process indicator with Contact i.e., FI, LI, PI, AI, TI, VI, FG, LG, PG, TG, DPI, DPG, FIS, LIS, PIS, TIS, VIS, DPIS |
| 701 – 899 | Not Used |
| 901 – 999 | Derived signals (e.g., median, average) |

Few Examples of Equipment Code Classification (B1 B2)

| Equipment Codes (For This Project)- TABLE: 4 |  |
| --- | --- |
| AA= Valves | GE= POWER CABLES |
| AD= Spray nozzles for FGTR & MCU | GF= Electrical/Control Cables and Glands |
| AE= Lifting device | GH= LTMCC/SWITCHBOARD |
| AN= Booster Fan | GK= PLC |
| AP= Pump | GS= SWITCHGEAR |
| AQ= Damper | GW= Electrical Panels and Junction Boxes |
| AT= Filtering unit | GX= PMCC, MCC, ACDB and DCDB |
| AY= Expansion joints | KA= Lighting material |
| BB= Tanks | KP=Grounding Material |
| BQ= Hanger/ SUPPORTS/ STEEL STRUCTURES | MA= MOTORS |
| BR= Piping/ Duct | MD= MOV |
| BU= Insulation / Sheathing | PA= Painting/Primer |
| BY= Slider bearing | UC= CIVIL Materials |
| GC= CONTROL CABLE | YA= Air Conditioning/HVAC |
| GD= CABLE TRAY | YY= Glass flake lining/ LINING |

Mechanical Equipment, Valves, Pumps & Instrument

The format for mechanical equipment tag numbering shall consist of the following:

UU-FFF-SS-DD-NNN

UU	Plant Code, For RNSG we use 50

FFF	System Code (TABLE - 1), Example For RNSG, “HTA10” is described as Flue Gas Ducting

SS	System Numbering Code (Designer to put the number as per direction of flow/ Sides).

DD	Equipment Unit Code (Table - 4)

NNN	Equipment Number

Rev-2

Tagging/ Numbering logic is indicated below:

| FFF-SS | AT A GLANCE TO UNDERSTOOD (KKS SYSTEM CODE) |
| --- | --- |
|  | HTA- Flue gas ducting system |
|  | HTA10- Flue gas ducting TO EXISTING CHIMNEY RHS |
|  | HTA20- Flue gas ducting TO EXISTING CHIMNEY LHS |
|  | HTA11- Flue gas ducting tap-off to FGD INLET LHS |
|  | HTA22- Flue gas ducting tap-off to FGD INLET RHS |
|  | HTA30- Flue gas ducting COMMON INLET TO BOOSTER FAN |
|  | HTA40- Flue gas ducting OUTLET FROM BOOSTER FAN TO MCU |

| DD | KKS COMPONENT CODE: |
| --- | --- |
|  | AQ- DAMPERS |
|  | AY- EXPANSION JOINTS |
|  | CT- TEMPERATURE TRANSMITTER (101 TO 999) |
|  | CP- PRESSURE INDICATOR LOCAL (501-699) |
|  | CP- PRESSURE TRANSMITTER (101-199) |
|  | AA- MANUAL VALVE (001 TO 099) |
|  | AA- MOTORISED VALVE (600-999) |

Plant Equipment Tagging Examples

Valves

Manual isolation valve (Flue Gas Line)

50HTA10AA600

Rev-2

Equipment’s

50PBLXX-AP001

Pump

PT

50HTA11CP101

Instruments:

Pressure Transmitter

Document & Drawing Number

| Deliverable & Document No. | Drawing or Document No |
| --- | --- |
| Engineering Issues |  |
| FGD & SAC Location of Bore Hole | S21001- EE01-05HSD- 123001 |
| FGD & SAC - PROCESS |  |
| FGD - Process Flow Diagram with Mass Balance | S21001- XF01 - 05HSD- 227001- SHEET X OF XX |
| SAC - Process Flow Diagram with Mass Balance | under development |
| FGD & SAC - Media Specification | S21001- PM01-05CPP-121004 |
| FGD - Process and Instrumentation Diagrams (with KKS or other Hindalco numbering System) | S21001- XG01 - 05HSD- 227101- SHEET X OF XX |
| SAC - Process and Instrumentation Diagrams (with KKS or other Hindalco numbering System) | under development |
| FGD-Equipment List | S21001- EN01 - 05HSD- 221001 |
| SAC -Equipment List | under development |
| FGD - Technical Specification with equipment sizing | S21001- TS01 - 05HSD- 227201 |
| SAC - Technical Specification with equipment sizing | under development |
| FGD - Computerized Fluid-dynamic Simulation (CFD) | S21001- EN01 - 05HSD- 221002 |
| FGD - Performance Curve | S21001- EN01 - 05CPP- 221003 |
| Inlet SOx vs. Outlet Sox |  |
| FGD - Specification of Performance Guaranteed Parameters | S21001- EN01 - 05CPP- 221004 |
| SAC - Specification of Performance Guaranteed Parameters | under development |
| FGD & SAC - EQUIPMENT |  |
| TECHNICAL SPECIFICATIONS |  |
| FGD - Booster Fan - Technical Specification | S21001- TS01 - 05HNC- 227202 |
| FGD - Flue Gas Ducts Expansion Joints - Technical Specification | S21001- TS01 - 05HTA- 227203 |
| FGD - Flue Gas Ducts Dampers - Technical Specification | S21001- TS01 - 05HTA- 227204 SHEET X OF XX |
| FGD - Hot Air Sealing Package for Dampers - Technical Specification (IF ANY) | S21001- TS01 - 05HTA- 227204 SHEET X OF XX |
| FGD - Process Recycle Pumps - Technical Specification | S21001- TS01 - 05PBQ- 227204 |
| FGD - Ash Filters - Technical Specification | S21001- TS01 - 05RTQ- 227205 |
| FGD - Hopper Cleaning Pumps - Technical Specification | S21001- TS01 - 05PBQ- 227206 |
| FGD - Wash Recycle Pumps - Technical Specification | S21001- TS01 - 05RTQ- 227207 |
| FGD - Wash Recycle Ash Filters - Technical Specification | S21001- TS01 - 05RTQ- 227208 |
| FGD - Process Water Pumps - Technical Specification | S21001- TS01 - 05PBQ- 227209 |
| FGD - Acid Transfer Pumps - Technical Specification | S21001- TS01 - 05GNK- 227210 |
| FGD - FGTR Washing Grid and Nozzles of SPC Modules - Technical Specification | S21001- TS01 - 05HSD- 227211 |
| FGD - MCU Flue Gas Cooling Grid and Nozzles - Technical Specification | S21001- TS01 - 05HTH- 227212 |
| SAC - Vapour-Liquid Separator - Technical Specification | under development |
| SAC - Reboiler Heater Exchanger - Technical Specification | under development |
| SAC - Acid Condenser - Technical Specification | under development |
| SAC - Circulation Pumps - Technical Specification | under development |
| SAC - Vacuum System - Technical Specification | under development |
| FGD & SAC - MCU, FGTR, TANKS, VESSELS AND STEEL STRUCTURES DRAWINGS |  |
| FGD - Structural Steel Materials - Technical Specification | under development |
| SAC - Structural Steel Materials - Technical Specification | under development |
| FGD - MCU Mist Cooling Unit - Mechanical Calculation according to Indian Standard (latest edition) | S21001- EN01 - 05HTH - 221005 |
| FGD - MCU Mist Cooling Unit - Outline Drawing (including hoppers,) with design data, nozzles chart and loads on foundation | S21001- EN01 - 05HTH - 221006 |
| FGD - MCU Mist Cooling Unit - Outline Drawing supporting steel structure, stairs and platforms | S21001- EN01 - 05UVX - 221007 |
| FGD - MCU Mist Cooling Unit - Construction Drawings (including hoppers) | S21001- EN01 - 05HTH - 221008 |
| FGD - MCU Mist Cooling Unit - Construction Drawings (supporting steel structure, stairs and platforms) | S21001- EN01 - 05UVX - 221009 |
| FGD - FGTR Flue Gas Treatment Reactor - Mechanical Calculation according to Indian Standard (latest edition) | S21001- EN01 - 05HSD - 221010 |
| FGD - FGTR Flue Gas Treatment Reactor - Outline Drawing (including hoppers,) with design data, nozzles chart and loads on foundation | S21001- EN01 - 05HSD - 221010 |
| FGD - FGTR Flue Gas Treatment Reactor - Outline Drawing (supporting steel structure, stairs and platforms) | S21001- EN01 - 05UVC - 221011 |
| FGD - FGTR Flue Gas Treatment Reactor - Construction Drawings (including hoppers) | S21001- EN01 - 05HSD - 221012 |
| FGD - FGTR Flue Gas Treatment Reactor - Construction Drawings (supporting steel structure, stairs and platforms) | S21001- EN01 - 05UVC - 221013 |
| FGD - FGTR - Slider Bearings Details | S21001- EN01 - 05HSD - 221014 |
| FGD - MCU - Slider Bearings Details | S21001- EN01 - 05HTH - 221015 |
| FGD - FGTR - Spring Details (If required) | S21001- EN01 - 05HSD - 221016 |
| FGD - MCU - Spring Details (If required) | S21001- EN01 - 05HTH - 221017 |
| FGD - Wet Stack - Mechanical Calculation according to Indian Standard (latest edition) | S21001- EN01 - 05HNE - 221018 |
| FGD - Wet Stack - Outline Drawing (including hoppers) with design data, nozzles chart and loads | S21001- EN01 - 05HNE - 221019 |
| FGD - Wet Stack - Outline Drawing (supporting steel structure, stairs and platforms) | S21001- EN01 - 05UHN - 221020 |
| FGD - Wet Stack - Construction Drawings (including hoppers) | S21001- EN01 - 05HNE - 221021 |
| FGD - Wet Stack - Construction Drawings (supporting steel structure, stairs and platforms) | S21001- EN01 - 05UHN - 221022 |
| FGD - Process Water Tank - Outline Drawing with design data, nozzles chart and loads | S21001- EN01 - 05PBQ - 221023 |
| FGD - Process Water Tank - Construction Drawings | S21001- EN01 - 05PBQ - 221024 |
| FGD - Waste Recycle Tank - Outline Drawing with design data, nozzles chart and loads | S21001- EN01 - 05RTY - 221025 |
| FGD - Waste Recycle Tank - Construction Drawings | S21001- EN01 - 05RTY - 221026 |
| SAC - Equipment Supporting Steel Structures (including stairs and platforms) - Outline Drawings | under development |
| SAC - Equipment Supporting Steel Structures (including stairs and platforms) - Construction Drawings | under development |
| FGD & SAC - GENERAL ARRANGEMENTS |  |
| FGD - General Arrangement Drawing (Overall Plot Plan) | S21001- EN01 - 05HSD - 221027 |
| SAC- General Arrangement Drawing (Overall Plot Plan) | under development |
| FGD - General Arrangement Drawings (Plans and Sections) | S21001- EN01 - 05HSD - 221028 |
| SAC - General Arrangement Drawings (Plans and Sections) | under development |
| FGD & SAC - BUILDINGS |  |
| FGD Electrical Buildings - Architectural Outline Drawings (Plans and Sections) | S21001- EN01 - 05UCA - 331001 |
| FGD Electrical Buildings - HVAC - Technical Specification/AIR CONDITIONER | S21001- TS01 - 05UCA- 337201 |
| FGD Electrical Buildings - illumination - Technical Specification | S21001- TS01 - 05UCA- 337202 |
| FGD Electrical Buildings - Grounding Material and Lightening Arrestor - Technical Specification | S21001- TS01 - 05UCA- 337203 |
| SAC Buildings - Architectural Outline Drawings (Plans and Sections) | under development |
| SAC Buildings - HVAC - Technical Specification | under development |
| SAC Buildings - Lighting - Technical Specification | under development |
| SAC Buildings - Earthing Material and Lightning Arrestor - Technical Specification | under development |
| FGD & SAC - LIFTING EQUIPMENT SPECIFICATIONS |  |
| FGD - Lifting device for SPC modules maintenance - Technical Specification | S21001- TS01 - 05HSD- 227213 |
| SAC - Lifting device for SAC equipment maintenance - Technical Specification | under development |
| FGD - FLUE GAS DUCTS |  |
| FGD - Flue Gas Ducts (including supporting structures, stairs and platforms) - Outline Drawings | S21001- EN01 - 05UVZ - 221029 |
| FGD - Flue Gas Ducts Supporting Steel Structures (including supporting structures, stairs and platforms) - Construction Drawings | S21001- EN01 - 05UVZ- 220131 |
| FGD & SAC - LININGS, PAINTINGS AND HEAT INSULATIONS |  |
| FGD - Glass Flake Linings - Technical Specification | S21001- TS01 - 05HSD- 227214 |
| FGD - Paintings - Technical Specification | S21001- TS01 - 05HSD- 227215 |
| SAC - Paintings - Technical Specification | under development |
| FGD - Heat Insulations - Technical Specification | S21001- TS01 - 05HSD- 227216 |
| SAC - Heat Insulations - Technical Specification | under development |
| FGD & SAC - CIVIL |  |
| FGD - Civil Materials - Technical Specification | S21001- TS01 - 05HSD- 557201 |
| SAC - Civil Materials - Technical Specification | under development |
| FGD - Foundation Layout Drawings with equipment loads and embedded parts | S21001- EN01 - 05HSD - 551001 |
| SAC - Foundation Layout Drawings with equipment loads and embedded parts | under development |
| FGD - Seismic / wind Calculation Report of the foundations | S21001- EN01 - 05CPP - 551002 |
| SAC - Seismic Calculation Report of the foundations | under development |
| FGD - Piling Outline Drawing (if piling is required) |  |
| SAC - Piling Outline Drawing (if piling is required) |  |
| FGD - Piling Specification (if piling is required) |  |
| SAC - Piling Specification (if piling is required) |  |
| FGD & SAC - Drainage’s drawings (funnels, trenches, sumps, etc.) | S21001- EN01 - 05CPP - 55005 |
| FGD & SAC - Cable trenches - Outline Drawings |  |
| FGD - Excavation and back fillings (with bill of quantities) | S21001- EN01 - 05HSD - 551003 |
| SAC - Excavation and back fillings (with bill of quantities) | under development |
| FGD - Equipment foundations - Formwork’s drawings (with bill of quantities) |  |
| SAC - Equipment foundations - Formwork’s drawings (with bill of quantities) |  |
| FGD - Equipment foundations - Steel bars and reinforcements drawings (with bill of quantities) | S21001- EN01 - 05HSD - 551004 |
| SAC - Equipment foundations - Formwork’s drawings (with bill of quantities) | S21001- EN01 - 05HSD - 551005 |
| SAC - Equipment foundations - Steel bars and reinforcements drawings (with bill of quantities) |  |
| FGD & SAC - PIPING |  |
| FGD - Piping Materials Technical Specification | S21001- TS01 - 05HSD- 227217 |
| SAC - Piping Materials Specification | under development |
| FGD - Piping Line List | S21001- EN01 - 05HSD- 220132 |
| SAC - Piping Line List | under development |
| FGD - Piping Layout (Plans and Sections) with pipe supports location identification | S21001- EN01 - 05HSD- 220133 |
| SAC - Piping Layout (Plans and Sections) with pipe supports location identification | under development |
| FGD - Pipe Racks and Access Platforms for Maintenance - Drawings with bill of quantities | S21001- EN01 - 05HSD- 220134 |
| SAC - Pipe Racks and Access Platforms for Maintenance - Drawings with bill of quantities | under development |
| FGD - Pipe Supports - Drawings with bill of quantities | S21001- EN01 - 05HSD- 220135 |
| SAC - Pipe Supports - Drawings with bill of quantities | under development |
| FGD - Piping Isometric Drawings with bill of quantities and support location identification | S21001- EN01 - 05HSD- 220136 |
| SAC - Piping Isometric Drawings with bill of quantities and support location identification | under development |
| FGD - Piping Painting Technical Specification (primer + final at site) | S21001- TS01 - 05HSD- 227218 |
| SAC - Piping Painting Specification (primer + final at site) | under development |
| FGD - Piping Heat Insulation Technical Specification | S21001- TS01 - 05HSD- 227219 SHEET X OF XX |
| SAC - Piping Heat Insulation Specification | under development |
| FGD - Expansion Joints Technical Specification | S21001- TS01 - 05HSD- 227220 |
| SAC - Expansion Joints Specification | under development |
| SAC - Stress Analysis Calculation of piping steam lines | under development |
| FGD & SAC - VALVES |  |
| FGD - Valve List/Schedule | S21001- VS01 - 05HSD- 228400 |
| SAC - Valve List/Schedule | under development |
| FGD - On/Off Valves - Data Sheets - Technical Spec | S21001- TS01 - 05HSD- 447201 |
| SAC - On/Off Valves - Data Sheets - Technical Spec | under development |
| FGD - Control Valves - Data Sheets - Technical Spec | S21001- TS01 - 05HSD- 447202 |
| SAC - Control Valves - Data Sheets - Technical Spec | under development |
| FGD & SAC - INSTRUMENTATION AND CONTROL SYSTEM |  |
| FGD - Operations & Controls Description | S21001- EN01 - 05HSD- 441001 |
| SAC - Operations & Controls Description | under development |
| FGD - Instrument List | S21001- EN01 - 05HSD- 441002 |
| SAC - Instrument List | under development |
| FGD - Measurement List | S21001- EN01 - 05HSD- 441003 |
| SAC - Measurement List | under development |
| FGD - Input/Output List | S21001- EN01 - 05HSD- 441004 |
| SAC - Input/Output List | under development |
| FGD - Instruments Data Sheets | S21001- EN01 - 05HSD- 441005 |
| SAC - Instruments Data Sheets | under development |
| FGD - Technical Specification for PLC | S21001- TS01 - 05HSD- 447203 |
| SAC - Technical Specification for PLC | under development |
| FGD - Loop Diagrams of main process sections | S21001- EN01 - 05HSD- 441006 |
| SAC - Loop Diagrams of main process sections | under development |
| FGD - Logic Diagrams | S21001- EN01 - 05HSD- 441007 |
| SAC - Logic Diagrams | under development |
| FGD - Control Architecture Scheme | S21001- EN01 - 05HSD- 441008 |
| SAC - Control Architecture Scheme | under development |
| FGD - Control Cables Sizing - Technical Specification | S21001- TS01 - 05HSD- 447204 |
| SAC - Control Cables Sizing - Technical Specification | under development |
| FGD - Hook-Up Diagrams | S21001- EN01 - 05HSD- 441009 |
| SAC - Hook-Up Diagrams | under development |
| FGD - Control Room Layout Drawing | S21001- EN01 - 05UCA- 441010 |
| SAC - Control Room Layout Drawing | under development |
| FGD - Instrument Location Plan Drawing | S21001- EN01 - 05HSD- 441011 |
| SAC - Instrument Location Plan Drawing | under development |
| FGD - Junction Boxes Location Plan Drawing | S21001- EN01 - 05HSD- 441012 |
| SAC - Junction Boxes Location Plan Drawing | under development |
| FGD & SAC - ELECTRICAL SYSTEM |  |
| FGD - Electrical Drive List | S21001- EN01 - 05HSD - 331002 |
| SAC - Electrical Drive List | under development |
| FGD - Electrical Cables List | S21001- EN01 - 05HSD - 331003 |
| FGD - Control Cables List | S21001- EN01 - 05HSD - 331004 |
| SAC - Electrical & Control Cables List | under development |
| FGD - Cable Trays / Conduits Layout with bill of quantities | S21001- EN01 - 05HSD - 331005 |
| SAC - Cable Trays / Conduits Layout with bill of quantities | under development |
| FGD - Junction Boxes - Technical Specification | S21001- TS01 - 05HSD- 337204 |
| SAC - Junction Boxes - Technical Specification | under development |
| FGD - PMCC, MCC, ACDB and DCDB - Technical Specification | S21001- TS01 - 05HSD- 337205 |
| SAC - PMCC, MCC, ACDB and DCDB - Technical Specification | under development |
| FGD - MOV - Technical Specification | S21001- TS01 - 05HSD- 337206 |
| SAC - MOV - Technical Specification | under development |
| FGD - LT/HT motors - Technical Specification | S21001- TS01 - 05HSD- 337207 |
| SAC- LT/HT cables - Technical Specification | under development |
| FGD - Electrical Single Line Diagram | S21001- EN01 - 05HSD - 331006 |
| SAC- Electrical Single Line Diagram | under development |
| FGD - Cable Sizing - Technical Specification | S21001- TS01 - 05HSD- 337208 |
| SAC- Cable Sizing - Technical Specification | under development |
| FGD - Individual Distribution Schemes/Control Schemes Drawing | S21001- EN01 - 05HSD - 331007 |
| SAC - Individual Distribution Schemes/Control Schemes Drawing | under development |
| FGD - Illumination Scheme Drawing | S21001- EN01 - 05HSD - 331008 |
| SAC - Illumination Scheme Drawing | under development |
| FGD - Plant Illumination Layout Drawing | S21001- EN01 - 05HSD - 331009 |
| SAC - Plant lighting Layout Drawing | under development |
| FGD - Grounding and Lightening System - Technical Specification |  |
| SAC - Grounding and Lightening System - Technical Specification |  |
| FGD - Grounding Scheme Drawing | S21001- EN01 - 05HSD - 331010 |
| SAC - Grounding Scheme Drawing | under development |
| FGD - Lightening Protection Drawing | S21001- EN01 - 05HSD - 331011 |
| SAC - Lightening Protection Drawing | under development |
| FGD - Plant Area Grounding and Lightening Protection Layout | S21001- EN01 - 05HSD - 331012 |
| SAC - Plant Area Grounding and Lightening Protection Layout | under development |
| FGD - Electrical Equipment Layout | S21001- EN01 - 05HSD - 331013 |
| SAC - Electrical Equipment Layout | under development |
| FGD - Electrical Room Layout (Plan and Sections) | S21001- EN01 - 05HSD - 331014 |
| SAC - Electrical Room Layout (Plan and Sections) | under development |
| FGD – Electrical/Control Cables and Glands - Technical Specification | S21001- TS01- 05HSD - 337209 |
| SAC – Electrical/Control Cables and Glands - Technical Specification | under development |
| FGD – Cable Trays - Technical Specification | S21001- TS01- 05HSD - 337210 |
| SAC – Cable Trays - Technical Specification | under development |
| FGD – LT Motors - Technical Specification | S21001- TS01- 05HSD - 337211 |
| SAC – LT Motors - Technical Specification | under development |
| FGD – HT Motors - Technical Specification | S21001- TS01- 05HSD - 337212 |
| SAC – HT Motors - Technical Specification | under development |
| FGD – LT & HT Switchgears - Technical Specification | S21001- TS01- 05HSD - 337213 |
| SAC – LT & HT Switchgears - Technical Specification | under development |
| FGD – Electrical Panels and Junction Boxes - Technical Specification | S21001- TS01- 05HSD - 337214 |
| SAC – Electrical Panels and Junction Boxes - Technical Specification | under development |
| FGD – LTMCC / Switchboard - Technical Specification | S21001- TS01- 05HSD - 337215 |
| SAC – LTMCC / Switchboard - Technical Specification | under development |
| FGD – UPS - Technical Specification | S21001- TS01- 05HSD - 337216 |
| SAC – UPS - Technical Specification | under development |
| FGD – UPS - Line Diagram | S21001- EN01 - 05HSD - 331015 |
| SAC – UPS - Line Diagram | under development |
| FGD & SAC - Auxiliary power calculation for continuous running of FGD plant including SAC at full load. | S21001- EN01 - 05CPP - 331016 |
| FGD & SAC - FIRE FIGHTING SYSTEM |  |
| FGD Fire Fighting - Fire Fighting & Detection System Technical Specification | S21001- TS01- 05SGA - 331017 |
| SAC Fire Fighting - Fire Fighting & Detection System Technical Specification | under development |
| FGD Fire Fighting - Hydrants and Water Spray System - Schematic Diagram | S21001- EN01- 05SGA - 331018 |
| SAC Fire Fighting - Alarm System - Schematic Diagram | under development |
| FGD Fire Fighting - Hydrants and Water Spray System - Layout Drawing | S21001- EN01- 05SGA - 331019 |
| SAC Fire Fighting - Hydrants and Water Spray System - Layout Drawing | under development |
| FGD Fire Fighting - Hydrants System - Hydraulic Calculation | S21001- EN01- 05SGA - 331020 |
| SAC Fire Fighting - Hydrants System - Hydraulic Calculation | under development |
| FGD Fire Fighting - Water Spray System - Hydraulic Calculation | S21001- EN01- 05SGA - 331021 |
| SAC Fire Fighting - Water Spray System - Hydraulic Calculation | under development |
| FGD Fire Fighting - Components Data Sheets | S21001- EN01- 05SGA - 331022 |
| SAC Fire Fighting - Components Data Sheets | under development |
| FGD Fire Fighting - Alarm System at MCC and Control Room - General Arrangement Drawing | S21001- EN01- 05SGA - 331023 |
| SAC Fire Fighting - Alarm System at MCC and Control Room - General Arrangement Drawing | under development |
| FGD Fire Fighting - Fire Detection Alarm System - Data Sheets | S21001- EN01- 05SGA - 331024 |
| SAC Fire Fighting - Fire Detection Alarm System - Data Sheets | under development |
| FGD Fire Fighting - Fire Detection Alarm System - Layout | S21001- EN01- 05SGA - 331025 |
| SAC Fire Fighting - Fire Detection Alarm System - Layout | under development |
| FGD Fire Fighting - Fire Detection Alarm System - Schematic Drawing | S21001- EN01- 05SGA - 331026 |
| SAC Fire Fighting - Fire Detection Alarm System - Schematic Drawing | under development |
| FGD Fire Fighting - Fire Detection Alarm Equipment - Technical Specification | S21001- TS01- 05SGA- 337217 SHEET X OF XX |
| SAC Fire Fighting - Fire Detection Alarm Equipment - Technical Specification | under development |
| FGD Fire Fighting - Fire Extinguishers - Technical Specification | S21001- TS01- 05SGA- 337218 SHEET X OF XX |
| SAC Fire Fighting - Fire Extinguishers - Technical Specification | under development |
| FGD Fire Fighting - ERW steel pipes and fittings - Technical Specification | S21001- TS01- 05SGA- 337219 SHEET X OF XX |
| SAC Fire Fighting - ERW steel pipes and fittings - Technical Specification | under development |
| FGD Fire Fighting - Pumps - Technical Specification | S21001- TS01- 05SGA- 337220 SHEET X OF XX |
| SAC Fire Fighting - Pumps - Technical Specification | under development |
| FGD Fire Fighting - Sprinklers - Technical Specification | S21001- TS01- 05SGA- 337221 SHEET X OF XX |
| SAC Fire Fighting - Sprinklers - Technical Specification | under development |
| FGD & SAC - PURCHASING TECHNICAL SPECIFICATIONS (PTS) |  |
| FGD - Booster Fan - PTS Purchasing Technical Specification | S21001- TS01 - 05HSC- 227221 |
| FGD - Flue Gas Ducts Expansion Joints - PTS Purchasing Technical Specification | S21001- TS01 - 05HTA- 227223 |
| FGD - Flue Gas Ducts Dampers - PTS Purchasing Technical Specification | S21001- TS01 - 05HTA- 227224 |
| FGD - Pumps - PTS Purchasing PTS Purchasing Technical Specification |  |
| FGD - Process Recycle Pumps - PTS Purchasing Technical Specification | S21001- TS01 - 05PBQ- 227225 |
| FGD - Hopper Cleaning Pumps - PTS Purchasing Technical Specification | S21001- TS01 - 05PBQ- 227226 |
| FGD - Wash Recycle Pumps - PTS Purchasing Technical Specification | S21001- TS01 - 05RTY- 227227 |
| FGD - Process Water Pumps - PTS Purchasing Technical Specification | S21001- TS01 - 05PBQ- 227228 |
| FGD - Acid Transfer Pumps - PTS Purchasing Technical Specification | latter |
| SAC - Pumps - PTS Purchasing Technical Specification | under development |
| FGD - Ash Filters - PTS Purchasing Technical Specification | S21001- TS01 - 05RTY- 227229 |
| FGD - Wash Recycle Ash Filters - PTS Purchasing Technical Specification | S21001- TS01 - 05RTY- 227230 |
| FGD - MCU Flue Gas Cooling Nozzles and FGTR Washing Nozzles of SPC Modules - PTS Purchasing Technical Specification | S21001- TS01 - 05HSD- 227231 |
| SCA - Vapour-Liquid Separator, Reboiler Heater Exchanger, Acid Condenser, Circulation Pumps and Vacuum System - PTS Purchasing Technical Specification | under development |
| FGD - MCU Mist Cooling Unit, FGTR Flue Gas Treatment Unit and Wet Stack - PTS Purchasing Technical Specification |  |
| FGD - Steel waste recycle water Tanks - PTS Purchasing Technical Specification | S21001- TS01 - 05PBQ- 227232 |
| FGD - Steel Process water Tanks - PTS Purchasing Technical Specification | S21001- TS01 - 05RTY- 227233 |
| SAC - Steel Tanks - PTS Purchasing Technical Specification | under development |
| FGD - FRP Tanks/ FRP Lining - PTS Purchasing Technical Specification | S21001- TS01 - 05HSD- 227234 |
| SAC - FRP Tanks/ FRP Lining - PTS Purchasing Technical Specification | under development |
| FGD Electrical Buildings - HVAC/AIR CONDITIONING - PTS Purchasing Technical Specification | S21001- TS01 - 05UCA- 337232 |
| SAC Buildings - HVAC - PTS Purchasing Technical Specification | under development |
| FGD Electrical Buildings - Lighting - PTS Purchasing Technical Specification | S21001- TS01 - 05UCA- 337233 |
| SAC Buildings - Lighting - PTS Purchasing Technical Specification | under development |
| FGD Electrical Buildings - Earthing Material and Lightening Arrestor - PTS Purchasing Technical Specification | S21001- TS01 - 05UCA- 337234 |
| SAC Buildings - Earthing Material and Lightening Arrestor - PTS Purchasing Technical Specification | under development |
| FGD - Lifting devices - PTS Purchasing Technical Specification | S21001- TS01 - 05HSD- 227235 |
| SAC - Lifting devices - PTS Purchasing Technical Specification | under development |
| FGD - Flue Gas Ducts (including supporting structures, stairs and platforms) - PTS Purchasing Technical Specification | S21001- TS01 - 05UVZ- 227236 |
| FGD - Linings - PTS Purchasing Technical Specification | INCLUDED IN 15.12, 15.13 |
| SAC - Linings - PTS Purchasing Technical Specification |  |
| FGD - Paintings - PTS Purchasing Technical Specification | S21001- TS01 - 05HSD- 227237 |
| SAC - Paintings - PTS Purchasing Technical Specification | under development |
| FGD - Heat Insulations - PTS Purchasing Technical Specification | S21001- TS01- 05HSD- 227238 |
| SAC - Heat Insulations - PTS Purchasing Technical Specification | under development |
| FGD - Piping - PTS Purchasing Technical Specification | S21001- TS01- 05HSD- 227239 |
| SAC - Piping - PTS Purchasing Technical Specification | under development |
| FGD - Piping Supports - PTS Purchasing Technical Specification | S21001- TS01- 05HSD- 227240 |
| SAC - Piping Supports - PTS Purchasing Technical Specification | under development |
| FGD - Control System - PTS Purchasing Technical Specification | S21001- TS01- 05HSD- 227241 |
| SAC - Control System - PTS Purchasing Technical Specification | under development |
| FGD - Instrumentation - PTS Purchasing Technical Specification | S21001- TS01- 05HSD- 227242 |
| SAC - Instrumentation - PTS Purchasing Technical Specification | under development |
| FGD - Power Cables - PTS Purchasing Technical Specification | S21001- TS01- 05HSD- 337235 |
| FGD - Control Cables - PTS Purchasing Technical Specification | S21001- TS01- 05HSD- 447205 |
| SAC - Power Cables- PTS Purchasing Technical Specification | under development |
| SAC - Control Cables - PTS Purchasing Technical Specification | under development |
| FGD - Cable Trays - PTS Purchasing Technical Specification | S21001- TS01- 05HSD- 337236 |
| FGD - Conduits - PTS Purchasing Technical Specification | S21001- TS01- 05HSD- 337237 |
| SAC - Cable Trays - PTS Purchasing Technical Specification | under development |
| SAC - Conduits - PTS Purchasing Technical Specification | under development |
| FGD - Switchboard, Distribution and Utilities Boards - PTS Purchasing Technical Specification | S21001- TS01- 05HSD- 337238 |
| SAC - Switchboard, Distribution and Utilities Boards - PTS Purchasing Technical Specification | under development |
| FGD - Illumination/Lighting (Outside and inside) - PTS Purchasing Technical Specification | Considered within 15.16 to 15.19 |
| SAC - Illumination/Lighting (Outside and inside) - PTS Purchasing Technical Specification |  |
| FGD - Earthing Material and Lightening System - PTS Purchasing Technical Specification |  |
| SAC - Earthing Material and Lightening System - PTS Purchasing Technical Specification |  |
| FGD - Fire Fighting System - PTS Purchasing Technical Specification (if any) |  |
| SAC - Fire Fighting System - PTS Purchasing Technical Specification (if any) |  |
| FGD & SAC - Foundations Piling Works - PTS Purchasing Technical Specification (if piling is required) | IF REQUIRED LATER |
| FGD & SAC - Civil Works - PTS Purchasing Technical Specification | S21001- PS01- 05CPP- 555001 |
| FGD & SAC - Mechanical Erection Works - PTS Purchasing Technical Specification | S21001- PS01- 05CPP- 225001 |
| FGD & SAC - Electrical, Instrumentation and Control Installation Works - PTS Purchasing Technical Specification | S21001- PS01- 05CPP- 335001 |
| FGD & SAC - QUALITY ASSURANCE |  |
| FGD & SAC - Project Quality Control Manual (with Job Organization Chart) | S21001- QA01- 05CPP- 662001 |
| FGD & SAC - Quality Control Plan | S21001- QA01- 05CPP- 662002 |
| FGD & SAC - Overall Inspection and Test Plan | S21001- QA01- 05CPP- 662003 |
| FGD & SAC - Final Quality Dossier | S21001- QA01- 05CPP- 662004 |
| FGD & SAC - HAZOP study and ARM analysis (Availability, Reliability & Maintainability) | S21001- QA01- 05CPP- 662005 |
| FGD & SAC - QUALITY CONTROL FOR FABRICATION |  |
| FGD & SAC - ITP Inspection and Test Plans for Fabrication | S21001- IT01- 05CPP- 664001 |
| FGD & SAC - Ball Valves - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664002 |
| FGD & SAC - Butterfly Valves - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664003 |
| FGD & SAC - Check Valves - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664004 |
| FGD & SAC - Fiberglass Piping Prefabricated - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664005 |
| FGD & SAC - Piping Expansion Joints - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664006 |
| FGD & SAC - Carbon Steel Tanks - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664007 |
| FGD & SAC - Pressure Vessels - ITP Inspection and Test Plan for Fabrication |  |
| FGD & SAC - Fiberglass Tanks - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664008 |
| FGD & SAC - Spray Nozzles - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664009 |
| FGD & SAC - Booster Fan - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664010 |
| FGD & SAC - Blowers - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664011 |
| FGD & SAC - Fans - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664012 |
| FGD & SAC - Centrifugal Pumps - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664013 |
| SAC - Evaporators - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664014 |
| SAC - Heat Exchangers - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664015 |
| FGD & SAC - Carbon Steel Plates Painted - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664016 |
| FGD & SAC - Alloy Steel Plates - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664017 |
| FGD & SAC - Main Steel Structures - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664018 |
| FGD & SAC - Flue Gas Ducts - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664019 |
| FGD & SAC - Flue Gas Dampers - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664020 |
| FGD & SAC - Instrumentation - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664021 |
| FGD & SAC - Analytical Instruments - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664022 |
| FGD & SAC - Instruments Frames - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664023 |
| FGD & SAC - Cables - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664024 |
| FGD & SAC - PLC Local Control Panels - ITP Inspection and Test Plan for Fabrication | S21001- IT01- 05CPP- 664025 |
| FGD & SAC - QUALITY CONTROL FOR ERECTION AND CIVIL WORKS |  |
| FGD & SAC - ITP Inspection and Test Plans for Civil & Erection Works | S21001- IT01- 05CPP- 664026 |
| FGD & SAC - Booster Fan - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664027 |
| FGD & SAC - Flue Gas Ducts - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664028 |
| FGD & SAC - Equipment Mechanical - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664029 |
| FGD & SAC - Electrical Equipment - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664030 |
| FGD & SAC - Instrumentation - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664031 |
| FGD & SAC - Piping - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664032 |
| FGD & SAC - Cables - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664033 |
| FGD & SAC - Insulation - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664034 |
| FGD & SAC - Mist Cooling Unit (MCU) - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664035 |
| FGD & SAC - Flue Gas Treatment Reactor (FGTR) - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664036 |
| FGD & SAC - Tanks - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664037 |
| FGD & SAC - Site Painting - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664038 |
| FGD & SAC - Glass Flake Lining - ITP Inspection and Test Plan for Erection Works | S21001- IT01- 05CPP- 664039 |
| FGD & SAC - Concrete Works - ITP Inspection and Test Plan for Civil Works | S21001- IT01- 05CPP- 664040 |
| FGD & SAC - System Deluge-Sprinkler - ITP Inspection and Test Plan for Civil Works | S21001- IT01- 05CPP- 664041 |
| SAC - Earthing Lighting Protection System Installation - ITP Inspection and Test Plan for Civil Works | S21001- IT01- 05CPP- 664042 |
| SAC - Roof and Cladding - ITP Inspection and Test Plan for Civil Works | S21001- IT01- 05CPP- 664043 |
| FGD & SAC - PROCEDURES AND MANUALS |  |
| FGD - Flue Gas Ducts - Erection Procedure | S21001-PS01- 05HTA- 225001 |
| FGD - MCU Mist Cooling Unit - Erection Procedure | S21001-PS01- 05HTC- 225002 |
| FGD - FGTR Flue Gas Treatment Reactor - Erection Procedure | S21001-PS01- 05HSD- 225003 |
| FGD - Booster Fan - Erection Procedure | S21001-PS01- 05HNC- 225004 |
| FGD- Process water Tanks & Vessels - Erection Procedure | S21001-PS01- 05PBQ- 225005 |
| FGD- Waste Recycle Tanks & Vessels - Erection Procedure | S21001-PS01- 05RTQ- 225006 |
| SAC - Tanks & Vessels - Erection Procedure | under development |
| FGD Process Water system - Piping - Erection Procedure | S21001-PS01- 05PBQ- 225007 |
| FGD Waste Water system - Piping - Erection Procedure | S21001-PS01- 05RTQ- 225008 |
| FGD Acid Water system - Piping - Erection Procedure | S21001-PS01- 05GNK- 225009 |
| SAC - Piping - Erection Procedure | under development |
| SAC - Erection Procedure | under development |
| FGD - MCU Mist Cooling Unit - Commissioning Procedure | S21001-CC01-05HTH-228500 |
| FGD - FGTR Flue Gas Treatment Reactor - Commissioning Procedure | S21001-CC01-05HSD-228501 |
| FGD - Booster Fan - Commissioning Procedure | S21001-CC01-05HNC-228502 |
| FGD - Hopper Cleaning Pumps - Commissioning Procedure | S21001-CC01-05PBQ-228503 |
| FGD - Wash Recycle Pumps - Commissioning Procedure | S21001-CC01-05RTQ-228504 |
| FGD - Process Water Pumps - Commissioning Procedure | S21001-CC01-05PBQ-228505 |
| FGD - Acid Transfer Pumps - Commissioning Procedure | S21001-CC01-05GNK-228506 |
| FGD - Recovered Water Return Pumps - Commissioning Procedure | S21001-CC01-05HNC-228507 |
| FGD - Process Recycle Pumps - Commissioning Procedure | S21001-CC01-05RTQ-228508 |
| SAC - Pumps - Commissioning Procedure | under development |
| SAC - Commissioning Procedure | under development |
| FGD & SAC - Fire Fighting System - Commissioning Procedure | S21001- EN01- 05SGA- 338500 |
| FGD - Performance Test Procedure | S21001-CC01-05HSD-228510 |
| SAC - Performance Test Procedure | under development |
| FGD - Operation & Maintenance Manual | S21001-MA01-05HSD-228511 |
| SAC - Operation & Maintenance Manual | under development |
| FGD & SAC - PROCEDURES AND MANUALS |  |
| FGD & SAC- Master Project Schedule | S21001-MS01-05CPP-118400 |
| FGD & SAC- Engineering Document List/MDL | S21001-EN01-05CPP-221030 |
| General Category/Project Management |  |
| Document / Document Name plate | S21001-PM01-05CPP- 121001 |
| Deliverable list with Drawing Number | S21001-PM01-05CPP- 121002 |
| Smartluth Organisation Chart | S21001-PM01-05CPP- 121003 |
| KKS Numbering System with Media Specification | S21001- PM01-05CPP-121004 |
| Drawing Standard Sheet and Document Cover Sheet | S21001- PM01-05CPP-121005 |