ANNEXURE-III

STANDARD TECHNICAL SPECIFICATION

FOR

E1- AC/DC MOTORS

&

E7 – VARIABLE FREQUENCY DRIVE

CONTENTS E1

1.00.00	 	DESIGN CRITERIA					 1

2.00.00		STANDARDS						 1

3.00.00		TYPE AND RATING   					 1

4.00.00	 	SPECIFIC REQUIREMENTS				 2

5.00.00		TESTS				      			 7

6.00.00		SPARES   					      	 8

7.00.00		DRAWINGS, DATA AND MANUALS			 8

## ATTACHMENT

ANNEXURE – A	DESIGN DATA                                                             10

CONTENTS E7

1.00		 	GENERAL					 	1

2.00			CODES AND STANDARDS				1

3.00			TECHNICAL REQUIREMENTS   			1

SECTION-E2 - AC/DC MOTORS

1.00.00	DESIGN CRITERIA

1.01.00	General

1.01.01	Motors shall be furnished in accordance with both this general specification and the accompanying driven equipment specification.

In case of any discrepancy, the driven equipment specification shall govern.

1.01.02	The motors will be installed in hot, humid and tropical atmosphere, highly polluted with coal dust.  Canopy to be provided to all outdoor installed motors.

1.01.03	Electrical equipment design shall be based on the service conditions and auxiliary power supply given in the annexure of this specification.

1.01.04	For motor installed outdoor and exposed to direct sun rays, the effect of solar heat shall be considered in the determination of the design ambient temperature.

2.00.00	STANDARDS

2.01.00   	All motors shall conform to the latest applicable IS, IEC and CBIP Standards/Publications except when otherwise stated herein or in the driven equipment specification.

2.02.00 	Major standards, which shall be followed, are listed below other applicable Indian Standards for any component part even if not covered in the listed standards shall also be followed :

IS-325

IS-12615

IEC-34

3.00.00	TYPE & RATING

3.01.00	A.C. Motors

3.01.01	Motors shall be general purpose, constant speed, squirrel cage, three phase  induction type.

3.01.02	All motors shall be rated for continuous duty.  They shall also be suitable for long period of inactivity.

3.01.03	The motor name-plate rating shall have at least 15% margin over the input power requirement of the driven equipment at rated duty point.

3.01.04	The motor characteristics shall match the requirements of the driven equipment so that adequate starting, accelerating, pull up, break down and full load torques are available for the intended service.

3.01.05	Motors located in hazardous area shall be flameproof type.

3.02.00	D.C. Motors

3.02.01	D.C. motor provided for emergency service shall be shunt/compound wound type.

3.02.02	Motor shall be sized for operation with fixed resistance starter for maximum reliability.

3.02.03	D.C. Motors shall be similar to A.C. Motors with respect to other features like enclosure type, cooling and class of insulation.

3.02.04	For lubrication of main motor to continue, even after AC mains power failure, a DC lube oil pump motor may be provided, if required.

4.00.00	SPECIFIC REQUIREMENTS

4.01.00	Running Requirements

4.01.01	Motor shall run continuously at rated output over the entire range of voltage and frequency variations as given in the annexure.

4.01.02	The motor shall be capable of operating satisfactorily at full load for 5 minutes without injurious heating with 75% rated voltage at motor terminals.

4.01.03	The motor shall be designed to withstand momentary overload of 60% of full load torque for 15 sec without any damage.

4.02.00	Starting Requirements

4.02.01	Motor shall be designed for direct on line starting at full voltage. Starting current shall not exceed 4.5 times full load current for all HT motors, subject to IS tolerance.

4.02.02	The motor shall be capable of withstanding the stresses imposed if started at 110% rated voltage. The motor shall be designed to withstand 120% rated speed for two minutes without any mechanical damage.

4.02.03	Motor shall start with rated load and accelerate to full speed with 80% rated voltage at motor terminals.

4.02.04	a)	The motor shall be capable of three equally spaced starts in an hour, the motor initially being at a temperature not exceeding the rated load operating temperature.

b)	The motor shall be capable of two starts in succession with coasting to rest between starts and the motor initially at rated operating temperature.

4.03.00	Stress During Bus Transfer

4.03.01	The motor may be subjected to sudden application of 150% rated voltage during bus transfer, due to the phase difference between the incoming voltage and motor residual voltage.

4.03.02	The motor shall be designed to withstand any torsional and/or high current stresses which may result, without experiencing any deterioration in the normal life and performance characteristics.

4.04.00	Locked Rotor Withstand Time

4.04.01	The locked rotor withstand time under hot condition at 110% rated voltage shall be more than motor starting time by at least 2.5 seconds for motors upto 20 seconds starting time and by 5 seconds for motor with more than 20 seconds starting time.

4.04.02	Starting time mentioned above is at minimum permissible voltage of 80% rated voltage.

4.04.03	Hot thermal withstand curve shall have a margin of at least 10% over the full load current of the motor to permit relay setting utilizing motor rated capacity.

4.05.00	Enclosure

4.05.01	All motor enclosures shall conform to the degree of protection IP-55.  Motor for outdoor or semi-outdoor service shall be of weather-proof construction.

4.05.02	For hazardous area approved type of increased safety enclosure shall be furnished.

4.06.00	Cooling

4.06.01	The motor shall be self ventilated type, either totally enclosed fan cooled (TEFC) or closed air circuit air cooled (CACA).

4.06.02	For large capacity motors, totally enclosed tube ventilation (TETV) shall be considered. In case of water-cooling is required for very large motors, prior approval of customer is to be obtained before proceeding with design and manufacture.

4.07.00	Winding and Insulation

4.07.01	All insulated winding shall be of copper.

4.07.02	All Motors shall have class F insulation but, limited to class B temperature rise.

4.07.03	Windings shall be impregnated to make them non-hygroscopic and oil resistant.

4.08.00	Tropical Protection

4.08.01	All motors shall have fungus protection involving special treatment of insulation and metal against fungus, insects and corrosion.

4.08.02	All fittings and hardwares shall be corrosion resistant.

4.09.00	Bearings

4.09.01	Motor shall be provided with antifriction bearings, unless sleeve bearings are required by the motor application.

4.09.02	Vertical shaft motors shall be provided with thrust and guide bearings. Thrust bearing of tilting pad type is preferred.

4.09.03	Bearings shall be provided with seals to prevent leakage of lubricant or entrance of foreign matters like dirt, water etc. into the bearing area.

4.09.04	Sleeve bearings shall be split type, ring oiled, with permanently aligned, close running shaft sleeves.

4.09.05	Grease lubricated bearings shall be prelubricated and shall have provisions for in-service positive lubrication with drains to guard against over lubrication.

4.09.06	Oiled bearing shall have an integral self cooled oil reservoir with oil ring inspection ports, oil sight glass with oil level marked for standstill and running conditions and oil fill and drain plugs.

4.09.07	Forced lubricated or water cooled bearing shall not be used without prior approval of Owner.

4.09.08	Lubricant shall not deteriorate under all service conditions. The lubricant shall be limited to normally available types with IOC equivalent.

4.09.09	Bearings shall be insulated as required to prevent shaft current and resultant bearing damage.

4.10.00 	Noise & Vibration

4.10.01	The noise level shall not exceed 85 db (A) at 1.5 meters from the motor.

4.10.02	The peak amplitude of the vibration shall be within I.S/IEC specified limits.

4.11.00	Motor Terminal Box

4.11.01	Motor terminal box shall be detachable type and located in accordance with Indian Standards clearing the motor base-plate/foundation

4.11.02	Terminal box shall be capable of being turned 360o in steps of 90o, unless otherwise approved.

4.11.03	The terminal box shall be split type with removable cover with access to connections and shall have the same degree of protection as motor.

4.11.04	The terminal box shall have sufficient space inside for termination/ connection of XLPE (6.6kV grade)/ XLPE (1100V grade)(for space heater/CT/RTD, etc) insulated armoured cables, Copper conductor for MV level, Aluminium for LV Power and copper for LV controls.

4.11.05	Terminals shall be stud or lead wire type, substantially constructed and thoroughly insulated from the frame.

4.11.06	The terminals shall be clearly identified by phase markings, with corresponding direction of rotation marked on the non- driving end of the motor.

4.11.07	The terminal box shall be capable of withstanding maximum system fault current for a duration of 0.25 sec.

4.11.08	For 6.6kV motor, the terminal box shall be phase segregated type.  The neutral leads shall be brought out in a separate terminal box (not necessarily phase segregated type) with shorting links for star connection.

4.11.09	Motor terminal box shall be furnished with suitable cable lugs and double compression brass glands.

4.11.10	The gland plate for single core cable shall be non-magnetic type.

4.11.11	In case of motor terminal box being not suitable for specified cable size/number, suitable adopter box/extension box shall be provided.

4.12.00	Grounding

4.12.01	The frame of each motor shall be provided with two separate and distinct grounding pads complete with tapped hole, GI bolts and washer.

4.12.02	The cable terminal box shall have a separate grounding pad for termination of grounding conductor.

4.13.00	Rating Plate

In addition to the minimum information required by IS, the following information shall be shown on motor rating plate :

a)	Temperature rise in oC under rated condition and method of measurement.

b)	Degree of protection.

c)	Bearing identification no. and recommended lubricant.

d)	Location of insulated bearings.

4.14.00	Accessories

4.14.01	General

Accessories shall be furnished, as listed below, or if otherwise required by driven equipment specification or application.

4.14.02	Space Heater

a)	Motor of rating 30 KW and above shall be provided with space heaters, suitably located for easy removal or replacement.

b)	The space heater shall be rated 240 V, 1 phase, 50 Hz and sized to maintain the motor internal temperature above dew point when the motor is idle.

4.14.03	Temperature Detectors

a)	All 6.6kV motors shall be provided with six (6) duplex or twelve (12) simplex winding temperature detectors, two (2)/ four (4) per phase.

b)	 6.6V motor bearing shall be provided with duplex type temperature detectors.

c)	The temperature detector mentioned above shall be resistance type, 3 wire, platinum wound, 100 Ohms at 0oC.

4.14.04	Indicator/Switch

a)	Dial type local indicator with alarm contacts shall be provided for the following: -

i)	 6.6kV motor bearing temperature.

ii)	Hot and cold air temperature of the closed air circuit for CACA and CACW motor.

b)	Flow switches shall be provided for monitoring cooling water flow of CACW motor and oil flow of forced lubrication bearing, if used.

c)	Alarm switch contact rating shall be minimum 0.5 A at 220V D.C. and 2A at 240V A.C.

4.14.05	Current Transformer for Differential Protection

a)	Motor above 1000KW shall be provided with three differential current transformers mounted over the neutral leads within the enclosure. Loose 3 nos. CT for mounting on switchgear side shall also be in  scope of motor supplier..

b)	The arrangement shall be such as to permit easy access for C.T. testing and replacement. Current transformer characteristics shall match Purchaser's requirements to be intimated to the successful Bidder.

4.14.06	Accessory Terminal Box

a)	All accessory equipment such as space heater, temperature detector, etc., shall be wired to and terminated in terminal boxes, separate from motor (power) terminal box.

b)	Accessory terminal box shall be completed with double compression brass glands and pressure type terminals.

4.14.07	Drain Plug

Motor shall have drain plugs so located that they will drain the water, resulting from the condensation or other causes from all pockets of the motor casing.

4.14.08	Lifting Provisions

Motor weighing 25 kg. or more shall be provided with eye bolt or other adequate provision of lifting.

4.14.09	Dowel Pins

The motor shall be designed to permit easy access for drilling holes through motor feet or mounting flange for installation of dowel pins after assembling the motor and driven equipment.

4.14.10	Painting

Motor including fan shall be painted with corrosion proof paints with colour shade 631 of IS-5.

4.15.00	Construction

4.15.01	Stator Core

The stator lamination shall be made of high-grade silicon / magnetic  steel sheet varnished on both sides and pressed to form rigid core.

4.15.02	Rotor

The rotor construction shall be such that in case of dislodging of the rotor bar from the end ring, it should not come out and hit the stator core/ stator winding and damage.

5.00.00	TESTS

Routine and Type Tests are to be conducted in presence of customer’s representative as per IS:325/IEC and required copies of test certificates are to be furnished for approval. In addition, following tests shall have to be carried out on the motors in presence of customer’s representative.

- Impulse test of 36kV (peak) test voltage by 1.2/50 micro sec. on sample coil of stator winding insulation as type test as per latest version of IEC-671.

b.	Tan delta, charging current and dielectric loss measurements on each phase of motor stator winding as routine test.

- Polarization Index Test as per IS: 7816 as routine test.

- Test for suitability of IPW – 55 as per IS 4691 as type test. Type test certificate for first numeral shall be acceptable in lieu to test, provided the test motor is identical to motor being supplied. Second numeral test shall be carried out on the motors as routine test.

- Fault Withstand Test for main terminal box as type test. Type test certificate shall be acceptable, if the test is conducted on exactly identical terminal box.

- Test for noise level as routine test.

- Test for vibrations as routine test.

- Tan delta measurement on coils.

- Surge withstand test for inter turn insulation.

- Test to diagnose rotor bar failure during manufacture.

Tests indicated at (h), (i), (j) shall be carried out during manufacture of the coils and shall be furnished for verification.

6.00.00	SPARES

The bidder shall furnish a list of recommended spare parts for two (2) years satisfactory and trouble free operation.

7.00.00	DRAWINGS, DATA & MANUALS

Drawings, data & manuals for the motors shall be submitted as indicated below:

7.01.00	Along with the bid

a)	List of the motors

b)	Individual motor data sheet as per format of the proposal data sheets.

c)	Scheme & write up on forced lubrication system, if any

d)	Type test report

7.02.00	After Award of the Contract

a)	Dimensional General Arrangement drawing

b)	Foundation Plan & Loading

c)	Cable end box details

d)	Space requirement for rotor removal

e)	Thermal withstand curves hot & cold

f)	Starting and speed torque characteristics at 80% & 100% voltage

g)	Complete motor data

h)	Erection & Maintenance Manual

- Test reports

### ANNEXURE-A

DESIGN DATA

1.0	AUXILIARY POWER SUPPLY

| ###### Supply | ###### Description | ###### Consumer |
| --- | --- | --- |
| L.T. Supply | 415V, 3 Phase, 4W, 50 Hz, effectively earthed. | Motors upto 160KW |
| H.T. Supply | 6.6 kV, 3 Phase, 3W, 50 Hz, Non-effectively earthed. | Motors above 200 kW |
| D.C. Supply | 220V, 2W, unearthed |  |

2.0	RANGE OF VARIATION

A.C. Supply

Voltage 		: 	± 10%

Frequency		:	± 5%

Combined voltage	:	10% (absolute sum)

& frequency

D.C. Supply

Voltage		:	(+) 10% to (-) 15%

# SECTION – E7 : Variable Frequency Drives

- GENERAL

  - Intent of the Specification

This specification covers the minimum requirements for the design, engineering, material procurement, fabrication, assembly, inspection, testing, painting, supply, shipment and delivery of Variable Frequency Drive perfectly matching with the driven motor & fan.

  - Scope

Vendor’s scope shall include design, manufacture, assembly, testing, and delivery to site Variable Frequency Drives as per the main package specification. The Vendor shall provide all the necessary items and services required for successful operation of the system.

1.3	It is not the intent of this specification to completely specify herein all the details of design and construction of the equipment. The Supplier shall be responsible for the design, engineering, fabrication, testing and proper functioning of the equipment including selection of all accessories and materials. Any materials or accessories, which may not have been specifically mentioned but are required for normal and trouble-free operation in accordance with good engineering practice, shall be deemed to be included in the Supplier’s scope.

- CODES AND STANDARDS

  - General

All specifications, codes and relevant IS standards as applicable, shall be the latest revisions in force at the time of the issue of this document. In case of absence of any relevant Indian Standards, relevant IEC (IEC 61800 (Part-1 to 5) & IEC 60146) and ANSI/IEEE standards shall be referred to.

In case of conflict between documents relating to the enquiry or the purchase order, the requirements of main package specification shall apply.

- TECHNICAL REQUIREMENT

3.1	The Variable Frequency drive (VFD) shall conform to this specification and all the attachments. Any non-conformity shall be clearly indicated in the Table of Compliance.

3.2	Motors are specified separately. All motors are rated for 6.6kV, 50Hz, 3 phase AC supply.

3.3	VFD panel components shall be accessible from the front without any rear or side access. The design shall make use of modular plug in/draw out assemblies for both the system control equipment and power electronics equipment.

3.4	VFD shall be designed for a maximum, continuous operation at design ambient temperature. VFD shall be suitable for grounded system. VFD shall be suitable for operation on a supply voltage & frequency within limits as specified.

3.5	VFD shall be able to run through voltage dips less than 20 %.

3.6	The converter shall meet the sound pressure limit of 81 dB(A), with reference to 20 μPa, at any location 1 m distant from the converter under any load and/or frequency condition during operation within the speed range of the VFD’s.

3.7	Type test on an identical machine is acceptable. All routine tests shall be carried out as per relevant IS/IEC and international standards.

3.8	Cable termination boxes shall be suitable for the cable size selected. However the cable sizes will be provided to vendor during detailed design.

3.9	VFD vendor to furnish the rating of breaker/fuse of incomer of VFD enabling to co-ordinate the upstream protection.

3.10	Power supply for space heater for the VFD driven motors shall be derived in the VFD panel, such that in case of motor is not running the heaters shall be ON.

3.11	The Vendor shall indicate in the Table of Compliance, an itemised list of any comments or exceptions to specification and its attachments.

3.12	VFD panel shall have provision for wiring Alarm & tripping contact of motor temperature. The cabling between motor & VFD shall be done by the Purchaser.

3.13	VFD shall have provision to communicate with Station control system and shall provide following signals as minimum Speed Control (4-20mA), Speed Feedback (4-20mA), Common Fault Alarm (DI-VF) all other Status & Alarm Signals through Communication links. Provisions shall be there to accept VFD Start/ Stop/Speed Control signals from DCS & Feedback Indication signals to DCS.

3.14	The VFD shall be fitted with stainless steel nameplate mounted on the front of the panel using rivets or screws (sticker is not allowed) with minimum 5mm height lettering reporting the following information as a minimum:

Manufacturer’s name

Project name

Year of manufacture

Equipment Tag no. Later

Rated voltage, Current, Frequency, Speed, weight etc.,

Manufacturer serial no.

3.15	Description: The VFD shall convert the input 6600V (±10%), 50Hz (±2%), 3-ph, 50kA for 1sec AC main power to an adjustable 6600V, 50Hz, 3-ph, AC. Proper isolation & protection device (VCB/VCU with fuse-backup)  will be provided at the power incomer of VFD. The VFD shall use insulated gate bipolar transistors (IGBT) in the inverter section with a Pulse Width Modulated (PWM) output and arranged to provide variable speed of a NEMA MG 1, Design B, 3-phase, high efficiency induction motor by adjusting output voltage, current and frequency. The VFD shall include a comprehensive microprocessor based digital diagnostic system which monitors its own control functions and displays faults and operating conditions. The VFD shall be listed and labeled as a complete unit and shall include all accessories and requirements.

3.16	The VFD shall be rated matching the motor & the driven equipment. As a minimum the full load output current of the drive shall be equal to the equivalent motor horsepower as listed by motor manufacturer.

3.17	Capability: 1.1 times the base load current for 60 seconds & 2.0 times the base load current for 3 seconds. Starting Torque: 100 percent of rated torque or as indicated. Speed & acceleration requirements shall match respective motor requirements. Vendor shall coordinate with the respective motor manufacturer for matching with starting torque, starting current & other related parameters. Current Limit shall be maintained within 60% to 110% percent of maximum rating.

3.18 	Protection and Reliability Features: The VFD shall include the following:

- Input transient protection by means of surge suppressors.

- Upon power-up the VFD shall automatically test for valid operation of memory, loss of analog reference input, loss of communication, dynamic brake failure, control power and the pre-charge circuit.

- Under and over voltage trips, inverter over temperature, overload, and overcurrent trips.

- Motor Overload Relay: Adjustable and capable as per standards.

- The VFD shall be capable of starting into a rotating load (forward or reverse) and accelerate or decelerate to set point without safety tripping or component damage (flying start).

- The VFD shall be capable of DC injection braking at start to stop a reverse spinning motor prior to ramp.

- The VFD shall be equipped with an automatic extended power ride through circuit, which will utilize the inertia of the load to keep the drive powered. Typical control power ride-through for a fan load shall be a minimum of 200 milliseconds.

- If the input reference power (4-20mA or 0-10V) is lost, this shall cause a warning to be issued and the user shall have the option of preselecting either (1) stopping and displaying the fault, (2) running at a programmable preset speed, (3) hold the VFD speed based on the last good reference received. The VFD shall be programmable to signal this condition via a keypad warning, relay output or over the serial communication link.

- The VFD shall be capable of sensing a loss of load and signal the loss of load condition.

- Instantaneous line-to-line and line-to-ground over current trips.

- Loss-of-phase protection.

- Reverse-phase protection.

- Short-circuit protection.

- Motor over temperature fault.

3.19	Automatic Reset and Restart: To attempt three restarts after controller fault or on return of power after an interruption and before shutting down for manual reset or fault correction. Bi-directional auto-speed search shall be capable of starting into rotating loads spinning in either direction and returning motor to set speed in proper direction, without damage to controller, motor, or load.

3.20	Status Lights: Door-mounted light indicators shall indicate: Power On, Run and Fault. The detailed information on the type of fault and other operating information on the VFD shall be annunciated on keypad display.

3.21	Panel Mounted VFD Controller: A panel mounted VFD controller or electromechanical hand-off-auto switch shall allow for selection between “Hand”, “Auto” and “Off”. When “Hand” is selected motor speed shall be controlled via the panel mounted VFD controller. When “Auto” is selected motor speed shall be controlled via an external speed reference signal from either the FLN(P1) and/or a hardwired connection. The VFD shall incorporate “bumpless transfer” of speed reference when switching between “Hand” and “Auto” or between “Auto” and “Hand”. When “Off” is selected the VFD shall stop, regardless of prior control selection.

3.22	Indicating Devices: Meters or digital readout devices and selector switch, mounted flush in controller door and connected to indicate the following controller parameters:

Output frequency (Hz)

Motor speed (rpm)

Motor status (running, stop, fault)

Motor current (amperes)

Motor torque (percent)

Fault or alarming status (code)

PI feedback signal (percent)

DC-link voltage (VDC)

Set-point frequency (Hz)

Motor output voltage (V)

3.23	Control Signal Interface: Provide the VFD with the following:

- Electrical Input Signal Interface: A minimum of 2 analog inputs 4-20 mA (24 VDC) and 4 programmable digital inputs.

- Remote Speed Control Signal Inputs: Shall be able to accept 4-20 mA (24 VDC) or similar types of speed control input signals from the control system.

3.24	Additional Control Capabilities - Remote start-stop capabilities utilizing digital inputs. PI control capabilities utilizing one of the analog inputs as the control variable, or the control variable monitored connection.

3.25	Output Signal Interface: A minimum of 1 analog output signal (0/4-20 mA), which can be programmed to any of the following:

Output frequency (Hz)

Output current (load)

Motor torque (percent)

Motor speed (rpm)

Set-point frequency (Hz)

Control variable value

3.26	VFD drive door when the disconnect is in the “ON” position. Another mechanical interlock shall prevent operator from placing the disconnect in the “ON” position while the VFD drive door is open.

3.27	The VFD shall be capable of producing a variable AC voltage/frequency output to provide continuous operation over the normal system 20-100% speed range. The VFD must be capable of operation at 1/10 speed to facilitate checkout and maintenance of the driven equipment. As a commissioning and troubleshooting feature, the VFD power circuit shall be capable of operating without a motor connected to the VFD output. The VFD shall be able to produce full rated torque at any speed in the operating range (constant torque capability).

3.28 	If high breakaway/starting torque is required, the VFD shall provide full rated torque at breakaway.

3.29	One minute overload capability (1 minute every 10 minutes) shall be provided consistent with the application requirements defined in this specification.

3.30 	Input Harmonics : Operation of the VFD shall not add more than 3% total harmonic voltage distortion. Total harmonic current distortion limits for each individual VFD shall not exceed 5% as calculated and measured at the point of common coupling,

3.31 	The VFD converter section shall be 18 or more pulse to eliminate the need for harmonic filters. Harmonic filters are highly undesirable due to resonance problems, and they require tuning whenever other inductive/capacitive loads are placed on the system or when the power system changes. However, if any input or output filter is necessary, same will be provided without any disturbance to the electrical system and/or motor design.

3.32 	VFD system shall provide an output waveform that will allow utilization of standard motors, without the need of any special insulation or de-rating. Motor life expectancy should not be compromised in any way by operation with the VFD system. The system must comply with all elements of the output harmonics section of this specification. The VFD must provide motor overload protection in any operating condition.

3.33 	The VFD output shall produce minimum electrically-induced pulsating torque to the output shaft (less than 1%) of the mechanical system eliminating the possibility of exciting a resonance caused by VFD induced torque pulsations.

3.34 	VFD shall inherently protect motor from high-voltage v/t stress, independent of cable length to motor. VFD shall not require non-standard insulation systems or insulation ratings above the VFD output voltage rating. The VFD system shall be designed to produce no standing waves or over-voltage conditions based on cable lengths.

3.35 	An integral input transformer shall be included with the VFD system to provide common mode voltage protection and allow the use of a standard motor. Special high-voltage motor insulation is not an acceptable method for protection against common mode voltages. The VFD system must be supplied with a drive isolation transformer to provide common mode voltage protection and phase shifting (for 18 pulse or higher converter bridge, if employed to meet the power quality requirements.

3.36 	VFD System Efficiency - Guaranteed minimum VFD system efficiency shall be above 96% at 100% load, and above 95% in the 100% to 50% load range. Efficiency evaluation shall include input transformer, harmonic filters, and power factor correction (if applicable), VFD converter, and output filter, as indicated below. Input power factor shall also be above 0.9.