Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant

Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System

FGD & SAC - Media Specification

| 0 | 18/01/2022 | Initial Release | S. DAS | S. Chakraborty |  | M. Deb |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Rev. | Date | Description of Revision | Prepared | Checked |  | Approved |  |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant |  |  | Drg. / Doc. No.: S21001-EN01-05CPP-111001 |  |  |  |  |
| Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System |  |  | Gore Doc. No.: RPDU5.MP.500 |  |  |  | page 1 of 8 |
| FGD & SAC - Media Specification |  |  | GORE Job No.: RPDU5 |  |  |  | Rev. : 0 |
|  |  |  | File: Media Specification_S221001-EN01-05CPP-111001_18.1.2022 |  |  |  |  |
| This document is a property of W.L. GORE & ASSOCIATES (Pacific) Pte, Ltd. and it may contain trade secrets or privileged, undisclosed or otherwise confidential information. If you have received this document in error, you are hereby notified that any review, copying or distribution of it is strictly prohibited. |  |  |  |  |  |  |  |

MEDIA NAME AND CODE FOR FGD & SAC SYSTEM

| Sl No | Media Codes | Media Nomenclature |  |
| --- | --- | --- | --- |
| 1 | RW | RAW WATER/FRESH WATER |  |
| 2 | PW | PROCESS WATER(ACIDIC) FROM MCU |  |
| 3 | AW | ACIDIC WATER FROM FGTR |  |
| 4 | UG | UNTREATED FLUE GAS TO BOOSTER FAN |  |
| 5 | UG | UNTREATED FLUE GAS FROM BOOSTER FAN TO MCU |  |
| 6 | TG | TREATED FLUE GAS FROM MCU TO FGTR |  |
| 7 | CG | SO2 REDUCED CLEAN FLUE GAS FROM FGTR TO WET STACK |  |
| 8 | FD | FLUE GAS DUCT DRAIN |  |
| 9 | MD | MCU HOPPER DRAIN |  |
| 10 | RD | FGTR HOPPER DRAIN |  |
| 11 | IA | COMPRESSED AIR/ INSTRUMENT AIR |  |
| 12 | PA | PLANT AIR/SERVICE |  |
| 13 | MP | AUXILIARY MP STEAM FOR SAC PLANT |  |
| 14 | HP | AUXILIARY HP STEAM FOR SAC PLANT |  |
| 15 | CH | CONDENSATE FOR SAC PLANT |  |
| 16 | CM | CONDENSATE FOR SAC PLANT |  |
| 17 | VP | VAPOUR |  |
| 18 | MW | MAKE UP WATER FOR SAC |  |
| 19 | HTH | Mist cooling Unit (MCU) | KKS SYSTEM/ FUNCTION DESCRIPTION |
| 20 | HSD | Flue Gas Treatment Reactor (FGTR) |  |
| 21 | HTA | Flue Gas Ducting System |  |
| 22 | HNE | Wet Stack System |  |
| 23 | HSF | Mist Eliminator |  |
| 24 | HSC | Booster Fan System |  |
| 25 | HSM | 10% Acid Concentration Process water system from FGTR |  |
| 26 | GNK | 1% Acid Concentration Process water system from MCU |  |
| 27 | HTD | Sprinkler/Scrubbing/Spray System in FGTR |  |
| 28 | HSQ | Sprinkler/Scrubbing/Spray System in MCU |  |
| 29 | PBL | Fresh water System |  |
| 30 | LBG | HP & MP Steam Saturated |  |
| 31 | LCN | HP & MP Condensate |  |
| 32 | PAR | Make -up water System |  |
| 33 | GCN | Chemical Supply final product 95% concentrated Sulfuric acid |  |
| 34 | GNE | Sulfuric acid plant |  |
| 35 | SGA | Fire Fighting System |  |
| 36 | QHS | Compressed Air System |  |
| 37 | ETP | Plant Air System |  |

- Raw Water/Fresh water- (RW)

| PH | Silica | Conductivity | Total | Calcium | Total | Chloride | Total | Meta | Turbidity | TS | TDS | SS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| at | as |  | Hardness | Hardness | Alkalinity | as | Phosphate | Phosphate |  |  |  |  |
|  | (SiO2) |  | as (CaCO3) | as (CaCO3) | as (CaCO3) | (Cl) | as (PO4) | as (PO4) |  |  |  |  |
| 25°C | ppm | µmhos/cm | ppm | ppm | ppm | ppm | ppm | ppm | NTU | ppm | ppm | ppm |
| 7.6 | 11.0 | 140 | 50 | 30 | 48 | 7.8 | - | - | 6 | 96 | 91 | 5 |
| 7.6 | 11.0 | 143 | 52 | 31 | 46 | 7.8 | - | - | 5 | 97 | 93 | 4 |
| 7.6 | 11.0 | 136 | 50 | 30 | 48 | 8.0 | - | - | 6 | 93 | 88 | 5 |
| 7.6 | 11.1 | 138 | 48 | 28 | 44 | 8.0 | - | - | 5 | 94 | 90 | 4 |
| 7.6 | 11.0 | 137 | 50 | 30 | 54 | 7.8 | - | - | 4 | 92 | 89 | 3 |
| 7.6 | 11.1 | 140 | 48 | 28 | 42 | 8.1 | - | - | 4 | 94 | 91 | 3 |
| 7.7 | 11.1 | 139 | 48 | 28 | 42 | 8.1 | - | - | 4 | 93 | 90 | 3 |
| 7.7 | 11.1 | 138 | 48 | 28 | 42 | 8.1 | - | - | 4 | 93 | 90 | 3 |
| 7.7 | 11.1 | 139 | 48 | 28 | 44 | 8.1 | - | - | 4 | 93 | 90 | 3 |
| 7.7 | 11.0 | 141 | 50 | 30 | 46 | 7.8 | - | - | 5 | 95 | 92 | 3 |
| 7.6 | 11.2 | 139 | 48 | 28 | 42 | 8.2 | - | - | 5 | 94 | 90 | 4 |
| 7.6 | 11.0 | 138 | 50 | 60 | 46 | 8.0 | - | - | 5 | 94 | 90 | 4 |
| 7.6 | 11.0 | 138 | 52 | 30 | 46 | 8.0 | - | - | 5 | 94 | 90 | 4 |
| 7.7 | 11.0 | 139 | 50 | 30 | 46 | 8.0 | - | - | 6 | 94 | 90 | 4 |
| 7.7 | 11.0 | 140 | 50 | 30 | 46 | 8.0 | - | - | 5 | 96 | 91 | 5 |
| 7.7 | 11.0 | 140 | 50 | 30 | 46 | 8.0 | - | - | 5 | 95 | 91 | 4 |

Source of Data: Hindalco

- PROCESS WATER(ACIDIC) FROM MCU-(PW)

| KKS system code | GNK | PROCESS WATER 1% ACIDIC FROM MCU |
| --- | --- | --- |
| MEDIA CODE | PW | PROCESS WATER FROM MCU |
|  | UNIT |  |
| Chlorides as Cl | (mg/l) | 2050 |
| Nitrates as NO3 | (mg/l) | 36 |
| Copper as Cu | (mg/l) | 1.72 |
| Lead as Pb | (mg/l) | 0 .380 |
| Fluoride as F | (mg/l) | 1000.0 |
| Mercury as Hg | (mg/l) | 0.200 |
| Oil & Grease | (mg/l) | 2.50 |
| Iron as Fe | (mg/l) | 249.7 |
| Sulfuric Acid Concentration | (mg/l) | 12985 |

- ACIDIC WATER FROM FGTR-(AW)

| KKS system code | HSM | ACIDIC WATER 10% ACIDIC FROM FGTR |
| --- | --- | --- |
| MEDIA CODE | AW | ACIDIC WATER FROM FGTR |
|  | UNIT |  |
| Chlorides as Cl | (mg/l) | 160 |
| Nitrates as NO3 | (mg/l) | 8 |
| Copper as Cu | (mg/l) | BDL<0.05 |
| Lead as Pb | (mg/l) | 0.180 |
| Fluoride as F | (mg/l) | 90.00 |
| Mercury as Hg | (mg/l) | 0.006 |
| Oil & Grease | (mg/l) | 2.11 |
| Iron as Fe | (mg/l) | 19.91 |
| Sulfuric Acid Concentration | (mg/l) | 116620 |

Source of Data: Hindustan Zinc Pilot Plant

- UNTREATED FLUE GAS TO BOOSTER FAN-(UG)

| KKS system code | HTA | RAW FLUE GAS | REMARKS |
| --- | --- | --- | --- |
| MEDIA CODE | UG | UNTREATED FLUE GAS |  |
|  | UNIT |  |  |
| Flue gas flow (before cooling) | Nm³/h, wet | 379,591 | DATA TAKEN FROM WLGORE PROCESS SHEET |
| Temperature | °C | 148 | DATA TAKEN FROM WLGORE PROCESS SHEET |
| Pressure | mmH2O | 9985 | At Tapping Point |
| O2 | %vol, wet | 6.62 |  |
| CO2 | %vol, wet | 10.8 |  |
| N2 | %vol, wet | 72.73 |  |
| SO2 | mg/Nm3 | 1246 |  |
| O2 | %vol, dry | 7.34 |  |
| CO2 | %vol, dry | 11.98 |  |
| N2 | %vol, dry | 80.67 |  |
| SO2 inlet conc. | mg/Nm³, dry @6% O2 | 1590 | DATA TAKEN FROM WLGORE PROCESS SHEET |
| SO2 inlet conc. | mg/Nm³, dry | 1446 | DATA TAKEN FROM WLGORE PROCESS SHEET |
| SO2 inlet conc. | mg/Nm³, dry | 1246 | DATA TAKEN FROM WLGORE PROCESS SHEET |

- UNTREATED FLUE GAS FROM BOOSTER FAN TO MCU -(UG)

| KKS system code | HTA | RAW FLUE GAS | REMARKS |
| --- | --- | --- | --- |
| MEDIA CODE | UG | UNTREATED FLUE GAS |  |
|  | UNIT |  |  |
| Flue gas flow (before cooling) | Nm³/h, wet | 379,591 | DATA TAKEN FROM WLGORE PROCESS SHEET |
| Temperature | °C | 148 | DATA TAKEN FROM WLGORE PROCESS SHEET |
| Pressure | mmH2O | 9985 | At Tapping Point |
| O2 | %vol, wet | 6.62 |  |
| CO2 | %vol, wet | 10.8 |  |
| N2 | %vol, wet | 72.73 |  |
| SO2 | mg/Nm3 | 1246 |  |
| O2 | %vol, dry | 7.34 |  |
| CO2 | %vol, dry | 11.98 |  |
| N2 | %vol, dry | 80.67 |  |
| SO2 inlet conc. | mg/Nm³, dry @6% O2 | 1590 | DATA TAKEN FROM WLGORE PROCESS SHEET |
| SO2 inlet conc. | mg/Nm³, dry | 1446 | DATA TAKEN FROM WLGORE PROCESS SHEET |
| SO2 inlet conc. | mg/Nm³, dry | 1246 | DATA TAKEN FROM WLGORE PROCESS SHEET |

- TREATED FLUE GAS FROM MCU TO FGTR-(TG)

| KKS system code | HSD | TREATED FLUE GAS |
| --- | --- | --- |
| MEDIA CODE | TG | TREATED FLUE GAS |
|  | UNIT |  |
| Flue gas flow (after cooling) | Nm³/h, wet | 401,991 |
| Temperature | °C | 53 |
| Pressure | mbara |  |
| O2 (dry) | %Vol | 7.35 |
| CO2 (dry) | %Vol | 11.98 |
| N2 (dry) | %Vol | 80.67 |
| SO2 (dry) | mg/Nm3 | 182 |
| O2 (wet) | %Vol | 6.08 |
| CO2 (wet) | %Vol | 9.9 |
| N2 (wet) | %Vol | 66.69 |
| SO2 outlet from MCU | mg/Nm³, dry @6% O2 |  |
| SO2 outlet from MCU | mg/Nm³, dry |  |
| SO2 outlet from MCU | mg/Nm³, dry |  |

- SO2 REDUCED CLEAN FLUE GAS FROM FGTR TO WET STACK-(CG)

| KKS system code | HSD | SO2 REDUCED CLEAN FLUE GAS |
| --- | --- | --- |
| MEDIA CODE | CG | TREATED FLUE GAS |
|  | UNIT |  |
| Total volume dry | Nm³/h, wet | 401,991 |
| Actual volume | Am3/h wet |  |
| Temperature | °C | 53 |
| Pressure | mbara | 1033 |
| H2O vapour | Kg/h |  |
| SO2 outlet conc. | mg/Nm³, dry @6% O2 | 500 |
| SO2 outlet conc. | mg/Nm³, dry | 455 |
| SO2 outlet conc. | mg/Nm³, wet | 392 |

- FLUE GAS DUCT DRAIN-(FD)

| KKS system code | HTA | FLUE GAS DUCT DRAIN |
| --- | --- | --- |
| MEDIA CODE | FD | FLUE GAS DUCT DRAIN |
|  | UNIT |  |
| temperature | °C | 54 |
| pH |  | 1.7 |

- MCU HOPPER DRAIN-(MD)

| KKS system code | HTH | MCU DRAIN |
| --- | --- | --- |
| MEDIA CODE | MD | MCU HOPPER DRAIN |
|  | UNIT |  |
| temperature | °C | 54 |
| pH |  | 1.7 |

- FGTR HOPPER DRAIN- (RD)

| KKS system code | HSD | FGTR DRAIN |
| --- | --- | --- |
| MEDIA CODE | RD | FGTR HOPPER DRAIN |
|  | UNIT |  |
| temperature | °C | 54 |
| pH |  | 0.7 |

- COMPRESSED AIR/ INSTRUMENT AIR- (IA)

| KKS system code | QHS | COMPRESSED AIR/ INSTRUMENT AIR |
| --- | --- | --- |
| MEDIA CODE | IA | INSTRUMENT AIR |
|  | UNIT |  |
| max pressure | Bar-g | 6 |
| temperature | °C | 40 |

- PLANT AIR/SERVICE- (PA)

| KKS system code | ETP | PLANT AIR/SERVICE |
| --- | --- | --- |
| MEDIA CODE | PA | SERVICE AIR |
|  | UNIT |  |
| max pressure | Bar-g |  |
| temperature | °C |  |
| Oil content | mg/m3 |  |

- AUXILIARY MP STEAM FOR SAC PLANT-(MP)

| KKS system code | LBG | STEAM PIPING FOR SAC PLANT |
| --- | --- | --- |
| MEDIA CODE | MP | AUXILIARY MP STEAM SATURATED |
|  | UNIT |  |
| Pressure | Bar-g |  |
| Temperature | °C |  |

- AUXILIARY HP STEAM FOR SAC PLANT-(HP)

| KKS system code | LBG | STEAM PIPING FOR SAC PLANT |
| --- | --- | --- |
| MEDIA CODE | HP | AUXILIARY HP STEAM SATURATED |
|  | UNIT |  |
| Pressure | Bar-g | 17.5 |
| Temperature | °C | 211 |

- CONDENSATE FOR SAC PLANT-(CH)

| KKS system code | LCN | CONDENDSATE PIPING FOR SAC PLANT |
| --- | --- | --- |
| MEDIA CODE | CH | HP CONDENSATE |
|  | UNIT |  |
| Pressure | Bar-g |  |
| Temperature | °C |  |

- CONDENSATE FOR SAC PLANT-(CM)

| KKS system code | LCN | CONDENDSATE PIPING FOR SAC PLANT |
| --- | --- | --- |
| MEDIA CODE | CM | MP CONDENSATE |
|  | UNIT |  |
| Pressure | Bar-g |  |
| Temperature | °C |  |

- MAKE UP WATER FOR SAC- (MW)

| KKS system code | PAR | MAKEUP WATER |
| --- | --- | --- |
| MEDIA CODE | MW | MAKEUP WATER FOR SAC |
|  | UNIT |  |
| Temperature | °C |  |
| Pressure | Bar-g |  |

DETAILS OF SAC PLANT MEDIA WILL BE DESIGNATED AND INCORPORATED AFTER RECEIVING PFD AND P&ID FROM BVR