## Tr-11
Comment Resolution Sheet (CRS)
Plant | Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant
Project | Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System
Contract | HIL/RPD/FGD#5/ON SHORE/01 Dated 01/Nov/2021
Transmittal No. | G21001/TR/0011 (Booster Fan TS+PTS) |  | Dated | 2022-01-10
Drawing/Document No. | HIL Comment | W L Gore Remark | B&V Comments |  | W L Gore Reply
|  |  | Drawing/Document No. | Comment
S21001-TS01-05HNC-227202 (RPDU5.PG.030) & S21001-TS01-05HSC-227222 (RPDU5.PA.001) | Please specify whether its Multi-louvre Inlet Damper or Radial Vane Control at the Fans inlet and Outlet both |  |  | NO COMMENTS | It is left to fan vendor to decide whether to go for RVC or Inlet damper control. Please note that being a single fan operation unit, there are no outlet damper/s.
| Also distinguish which damper is pneumatic, which electrically operated |  |  |  | To achieve quick isolation of FGTR in case of any black outs or similar outages, all dampers are pneumatic as agreed earlier.
| Control Logic sequence for the dampers to be provided |  |  |  | Control logic is under preparation & the same will be provided along with the specification of PLC based main control Panel of the Plant.
| VFD is not an alternate option, instead compulsory. However, offer to be brought for both options |  |  |  | This is understood. Offer with damper operation is being taken to determine differential price only.
| Mark Silencer as YES. It is required in order to reduce noise |  |  |  | Inlet silencers are impractical for Booster Fan as its suction is encased in ducting. Noise reduction takes place by Acoustic insulation only.
| Why Flue Gas Duct is marked as Excluded from Scope of Supply |  |  |  | Flue gas ducting is excluded from fan vendor scope of supply. It will be manufactured & supplied by others
| Include Booster Fan Inlet and Outlet flange of Vibration Isolation expansion joint at Booster Fan in the Scope of supply |  |  |  | The same is already included in the Spec submitted. Pl look into the scope section
ANNEXURE-I : TECHNICAL DATA SHEET | Please clarify the value given as “SOx level- 1246 mn/Nm3” |  |  |  | 1246 mg/Nm3 refers to the SOx level at actual Oxygen content of flue gas. This corresponds to 1590 mg/NM3 at 6% Oxygen dry which is the contract value.
| Fan should be designed for handling Max. allowable SOx content i.e., 1590 mg/NM3 |  |  |  | See above.
| Min. flow Margin between Fan Designed and 100% BMCR should be 15-20% instead of 10% to cover all coal quality variations. |  |  |  | The margin provided is sufficient considering that there is no ambiguity and uncertainty in flows as it was measured at highest possible boiler load. It may not be out of context to inform that the measured gas flow is already 20% more than that calculated for boiler performance. Further the specification calls for "No Negative Tolerance" which itself adds another 3% margin. As discussed and agreed in the web meeting on 20.1.22 any further increase in size will call for huge motor which is not at all desirable. Hence the specification may be kept unaltered.
| Similarly, % Margin on Head to be 33% instead of 18.8% to cover all coal quality variations and change in flue gas flow rate |  |  |  | The margin provided is sufficient considering that there is no ambiguity and uncertainty in flows as it was measured at highest possible boiler load. It may not be out of context to inform that the measured gas flow is already 20% more than that calculated for boiler performance. Further the specification calls for "No Negative Tolerance" which itself adds another 3% margin. As discussed and agreed in the web meeting on 20.1.22 any further increase in size will call for huge motor which is not at all desirable. Hence the specification may be kept unaltered.
| The basis of fan differential, static pressure at fan inlet and outlet to be given. The pressure drop calculations to be provided of flue gas systems, ducting etc. |  |  |  | The break up of draught loss is as follows : Chimney suction compensation = 25 mm, Loss in flue to booster fan = 35 mm. In the discharge side loss in modules = 143 mm, in demister = 16 mm, in stack = 16 mm , in MCU = 7 mm, in flues from booster fan to MCU & MCU to FGTR = 24 mm. Hope this satisfies & clarifies sufficiently.
| How static pressure at fan inlet is coming near -60 mmWC |  |  |  | The existing boiler & ID fan system is assisted by a chimney draught (suction) of 25 to 30 mm. This is as per readings taken during tests. This additional suction available now will not be available when the damper to the existing chimney is closed. To ensure that the existing ID Fans operate at the same regime as now while operating FGTR, this additional suction has been considered in the booster fan.Please see above for break up of head losses to understand why the static pressure at fan inlet is coming near -60 mmWC
4.Annexure-3-Std spec of Elec | All motor measurements such as current, temperature, bearing temperature, winding temperature cold air and hot air temperature should have Analog monitoring for booster fan motor. |  |  |  | Aanalogue meters are very uncommon. All RTD/BTD outputs are 4-20mA, suitable for supplying a digital display only and be displayed in PLC based control panel. However, Analogue Meter for Current measurement can be provided in VFD panel as desired by you.
| Since there is no DC motor and HT motor in the system so remove their attribute from the sheet like 3.02.00. |  |  |  | This is a "Standard Spec" and hence, all types of motors are covered which may not be relevant to Booster Fan Case. However, the document has been revised accordingly.
| We will prefer VPI technology in motor for Booster fan motor. |  |  |  | Noted and has been included in the revised specification.
| Design basis for ambient temperature is not mentioned. It should be 50 Deg C. |  |  |  | Noted and has been included in the revised specification.
| Core should be of low loss silicon steel. |  |  |  | Noted and has been included in the revised specification.
| DC supply will be 135 VDC instead of 220 VDC.As Renusagar has 135 VDC supply from battery bank #5 |  |  |  | Noted and has been corrected in the revised specification.
| Since there is no motor above 1000KW so remove 4.14.05. |  |  |  | Noted and has been corrected in the revised specification.
| We will prefer CACA and TEFC cooled motor. Hence remove the specs about water cooled motor. |  |  |  | Noted. Specification of water cooled motor shall be removed the specification
| Technical specs applicable to booster fan motor should be in this sheet. removed all irrelevant and generalised statements. |  |  |  | Noted
| VFD should have the Input voltage rating 690 V instead of 6.6 KV. - |  |  |  | Noted and same has been incorporated in the revised specification
3.ANNEXURE-2 LAYOUT DRG. OF FAN | All dimensions are not given. */** put in dimensions . |  |  |  | Noted and necessary correction has been made in the revised specification.
| In the GA drawing, the elevation of the booster fan is not given. If the elevation of the buster fan is above 600 mm from ground level then consider the proper platform with railings surrounding the booster fan, access to reach the platform for the safe maintenance and operation of the booster fan. |  |  |  | Noted
| Duct supporting arrangement not shown in the drawings. |  |  |  | Noted and same has been incorporated in the revised specification
| Space required around the booster fan not mentioned for future maintenance purposes for placement of crane etc. |  |  |  | Same shall be shown when the GA drawing of Booster fan and also plot plan will be complete after receipt of Dimensional GA drawing of Booster Fan from the supplier.
| Electrical Cable Cut-outs and cable location not shown in the GA Drawing. |  |  |  | Please note that this is the Specification of Booster Fan but not the GA drawing of Booster Fan. The drawing /sketch attached to show Suppliers our requirement of (1) the orientation of fan (2) Duct orientation and size to select suction and discharge accordingly (3) furnishing of few important dimension enabling us to proceed for a preliminary GA drawing of booster fan even if the GA of fan is not included in the offer stage by the supplier. When the Layout and GA drawing of Booster Fan will be made , cable cut out/location will be shown.
s