## Sheet1
Comment Resolution Sheet (CRS)
Plant | Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant
Project | Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System
Contract | HIL/RPD/FGD#5/ON SHORE/01 Dated 01/Nov/2021
Drg/ Doc No. | S21001-EN01-05HSD-221011-R0 (SHT-1), (RPDU5.MV.003)
Rev. | 0
Drawing Title: | FGD - FGTR Flue Gas Treatment Reactor - Outline Drawing
Sr No | HIL /B&V Comments 13/01/2022 | GORE reply
1 | Elevator should be provided for any structure more than 30 m in height and where access is required. Elevator should be provided till the CEMS elevation of FGTR | Elevator is not in scope. If the same can be installed by HIL if required. However there is hardly any space to accommodate one.
2 | Caged Ladders / Monkey ladders should be provided with vertical life-line. | Noted & agreed.
3 | Identify the equipment between FWT/PWT and Filters ? Are these pumps ? Please label them | Yes, These are pumps. They will be properly labeled as per equipment abbreviation
4 | Hand rail height shall be 1m from the floor with Intermediate pipe at 500 pipe size 32Φ with 100x6 thick toe guard. | Noted & agreed.