|  |  | Owner: HINDALCO INDUSTRIES LIMITED Ahura Centre, 1st Floor, B Wing, Mahakali Caves Road, Andheri (East), Mumbai - 400 093, India |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | EPCM Contractor: W. L. GORE & ASSOCIATES (Pacific) Pte, Ltd. India Branch 703, A-Wing, 215 Atrium, Andheri Kurla Road, Mumbai 400059, India |  |  |  |  |  |
|  |  | Nominated Subcontractor - Engineering, Quality Control, Supervision: SMARTLuth Solution and Service Pvt. Ltd. Unit No: 503, 5th Floor, ECO Centre,. EM-4 Sector-V, Salt Lake City, Kolkata - 700091, India |  |  |  |  |  |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System KKS (Kraftwerk-Kennzeichen-System) Identification System ISSUED FOR; APPROVAL; INFORMATION; MANUFACTURING; CONSTRUCTION; AS-BUILT. |
| 03 | 25-01-2022 | Electrical & Instrumentation updated | S.DAS | S. Chakraborty |  |  | M.DEB |
| 02 | 10/12/2021 | Function Description included | S.DAS | S. Chakraborty |  |  | M.DEB |
| 01 | 19/11/2021 | General Revision | S.DAS | S. Chakraborty |  |  | M.DEB |
| 00 | 17/11/2021 | Initial Release | S.DAS | S. Chakraborty |  |  | M.DEB |
| Rev. | Date | Description of revision | Prepared | Checked |  |  | Approved |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant |  |  | Drg. / Doc. No.: S21001-PM01-05CPP-121004 |  |  |  |  |
| Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System |  |  | Gore Doc. No.: RPDU5.MP.500 |  |  | page 1 of 30 |  |
| KKS (Kraftwerk-Kennzeichen-System) Identification System |  |  | GORE Job No.: RPDU5 |  |  | Rev. : 03 |  |
|  |  |  | File: KKS Identification System R3 dt. 25.01.22 |  |  |  |  |
| This document is a property of W.L. GORE & ASSOCIATES (Pacific) Pte, Ltd. and it may contain trade secrets or privileged, undisclosed or otherwise confidential information. If you have received this document in error, you are hereby notified that any review, copying or distribution of it is strictly prohibited. |  |  |  |  |  |  |  |

Project Name: 	Flue Gas Desulphurization Equipment with GORETM SPC Technology

Project No: 				 	          S21001

Documentation Numbering Procedure: 	VGB KKS System

Intent of Document:

This document outlines the procedure for tagging Equipment, Specialty Items, Valves, Pipelines & Instrument systems. This procedure serves to control the identification of systems and components by using the Kraftwerk-Kennzeichen-System Identification System, hereafter referred to as KKS tagging system.

This system provides a means to identify plant facilities, equipment, piping, or any other plant components as defined within the attachments to this procedure.

The fields that make up for an equipment tag are:

- Plant Code

- System Code

- System Numbering

- Device Type Code

- Device Number

- Component Code

The identification codes to be used and the associated text explanations are specified within this KKS Tagging Procedure. Should it become necessary to add or modify certain identification codes in the course of the project, same shall be done.

Gaps in the Device Number for each combination of Unit Code, System Code, System Numbering Code, Device Type Code, and Component Code are acceptable, but shall be avoided, in general. The sequential increment of numbers used as tag number shall be from south to north and from west to east and from the lower elevations to higher elevations.

General format of drawing/document number:

SXXYYY: 	Project Number has been identified with S21001.

ZZNN:		Document type code of FGD system: (Document Type)

- EN01= Engineering Documents and Drawings.

- QA01= QA Documents.

- QC01= Quality Control Document.

- IT01= Inspection Test Plan.                           REV-0

- PS01= Erection Procedure/Work Method Statement.

- MA01= Manual/ OPERATING/ GENERAL

- XF01= PFD Diagram.

- XG01= P& I Diagram.

- TS01= Technical Specification.

- MS01= Master Project Schedule.

- CS01= Cable Schedule.

- VS01= Valve Schedule

- PM01= Project management

- IP01= information technology/Software_______REV 0

- EE01= Engineering Issues

- CC01= Commissioning Procedure

AA:			Discipline Codes as below

        - 11: General/PM/Communications

        - 22: Mechanical

        - 33: Electrical

        - 44: Control & Instrumentation

        - 55: Civil & Structures

        - 66: QA/QC

        - 77: HSE/EHS/ FIRE FIGHTING SYSTEM

        - 88: IT/ SOFTWARES

        - 99: SAC (TO BE UPDATED LATER)

NNNN:			Serial Numbers

Rev-3

Pre-defined     void

PLANT TAGGING, KKS-CODING PHILOSOPHY

- Type of Code and Breakdown Level

In consideration of the various requirements placed on the identification of plants, sections of plants and items of equipment in power stations, KKS has two different types of code:

- Process-related code

Process-related identification of systems and items of equipment according to their functions in various engineering disciplines.

- Point of installation code

Identification of points of installation of electrical and control and instrumentation equipment in

installation units (e.g. in cabinets, panels, consoles).

NOTE: Level “3” will be used for Control and Instrumentation, if necessary.

| Serial No. of breakdown | 0 |  |  | 1 |  |  |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Name of breakdown | Total Plant |  |  | System Code/Function |  |  |  |  |  |  | Equipment Unit Code |  |  |  |  | Component Code |  |  |  |
| Designation of Data Character | G |  |  | F0 |  | F1F2F3 |  | FN |  |  | A1A2 |  | AN |  |  | B1B2 |  | BN |  |
| Type of Data Character | ('A' OR 'N') |  |  | NN |  | AAA |  | NN |  |  | AA |  | NNN |  |  | AA |  | NN |  |
| Identification of power station units and unit independent plants |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Plant Code |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| System-classifying Classifying sub-division of system and plants of unit (As per KKS Code table) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Numbering subdivision of system and plants into sub-systems in systematic manner |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Classification of equipment as per KKS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Numbering of equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Classification of components as per KKS key |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Numbering of components, signals or signal applications |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

VGB KKS CODES

| Function Key, Main Groups as per KKS code |  |
| --- | --- |
| A | Grid and distribution system |
| B | Power transmission and auxiliary power supply |
| C | Instrumentation and control equipment |
| D | Not Used |
| E | Fuel supply and residues disposal |
| F | Handling of nuclear equipment |
| G | Water supply and disposal |
| H | Heat generation |
| J | Nuclear heat generation |
| K | Reactor auxiliary system |
| L | Steam, water, gas cycle |
| M | Main machine set |
| N | Process energy/fluid supply for external users (e.g., district heating) |
| P | Cooling water system |
| Q | Auxiliary system |
| R | Gas generation and treatment |
| S | Ancillary system |
| T | Not Used |
| U | Structure |
| V | Civil work and Construction work |
| W | Renewable energy plant |
| X | Heavy machinery (not main machine sets) (e.g., emergency diesel and generator sets) |
| Y | Not Used |
| Z | Workshop and office equipment |

KKS SYSTEM OR FUNCTION CODES (TABLE: 1)

Rev-3- Position changed

Rev-2

| SL No | KKS Codes | KKS SYSTEM/ FUNCTION DESCRIPTION |
| --- | --- | --- |
| 1 | HTH | Mist cooling Unit (MCU) |
| 2 | HTY | Flue Gas Treatment Reactor (FGTR) |
| 3 | HTA | Flue Gas Ducting System |
| 4 | HNE | Wet Stack System |
| 5 | HSF | Mist Eliminator |
| 6 | HSC | Booster Fan System |
| 7 | HSM | 10% Acid Concentration Process water system from FGTR |
| 8 | GNK | 1% Acid Concentration Process water system from MCU |
| 9 | HTD | Sprinkler/Scrubbing/Spray System in FGTR |
| 10 | HSQ | Sprinkler/Scrubbing/Spray System in MCU |
| 11 | PBL | Fresh water System |
| 12 | LBG | HP & MP Steam Saturated |
| 13 | LCN | HP & MP Condensate |
| 14 | PAR | Make -up water System |
| 15 | GCN | Chemical Supply final product 95% concentrated Sulfuric acid |
| 16 | GNE | Sulfuric acid plant |
| 17 | SGA | Fire Fighting System |

- Process-related identification of systems and items of equipment according to their functions in various engineering disciplines.

- Plant Code (F0)

A Two-digit plant code is used to designate a specific generating plant in databases.

The generating plant code allows for the differentiation of equipment in a database:

| 50 | Signifies Unit-5 |
| --- | --- |

- System Code (F1, F2, F3)

System Classification is the classification of systems and plants as per KKS Key and forms the first part of System code. It is also termed as Function Key.

Coding letters and designations of F1 in System classification is as follows:

A			Grid and distribution systems

B			Power transmission and auxiliary power supply

C			Instrumentation and control equipment

D			Instrumentation and control equipment

E			Conventional fuel supply and residues disposal

F			Handling of nuclear equipment

G			Water supply and disposal

H			Conventional heat generation

J			Nuclear heat generation

K			Nuclear auxiliary systems

L			Water, steam, gas cycles

M			Main machine sets

N			Process energy supply for external users (e.g. district heating)

P			Cooling water systems

Q			Auxiliary systems

R			Gas generation & treatment

S			Ancillary systems

T			Not Used

U			Structures

V			Civil work and Construction work

W		Systems for regenerative-energies

X			Heavy machinery

Y			Not Used

Z			Workshop and office equipment

See “TABLE-1” for the complete range of applicable system codes.

KKS SYSTEM OR FUNCTION CODES (TABLE-1)

| SL No | KKS Codes | KKS SYSTEM/ FUNCTION DESCRIPTION |
| --- | --- | --- |
| 1 | HTH | Mist cooling Unit (MCU) |
| 2 | HTY | Flue Gas Treatment Reactor (FGTR) |
| 3 | HTA | Flue Gas Ducting System |
| 4 | HNE | Wet Stack System |
| 5 | HSF | Mist Eliminator |
| 6 | HSC | Booster Fan System |
| 7 | HSM | 10% Acid Concentration Process water system from FGTR |
| 8 | GNK | 1% Acid Concentration Process water system from MCU |
| 9 | HTD | Sprinkler/Scrubbing/Spray System in FGTR |
| 10 | HSQ | Sprinkler/Scrubbing/Spray System in MCU |
| 11 | PBL | Fresh water System |
| 12 | LBG | HP & MP Steam Saturated |
| 13 | LCN | HP & MP Condensate |
| 14 | PAR | Make -up water System |
| 15 | GCN | Chemical Supply final product 95% concentrated Sulfuric acid |
| 16 | GNE | Sulfuric acid plant |
| 17 | SGA | Fire Fighting System |
| 18 | QHS | Compressed Air System |
| 19 | ETP | Plant Air System |
| 20 | HTY | Control & Protection equipment |

- System Numbering (FN)

System Numbering is numbering subdivision of systems and plants into subsystems and sections of plants. It forms the second part of System code. Numbering starts a new when one of the preceding code elements changes.

Following rules must be applied to the system numbering in ‘FN’:

In process-related identification the direction of flow takes priority over local conventions for orientation.

FN numbering is governed by the following principles:

- Numbering starts a new when one of the preceding code elements changes.

- Numbering is grouping (e.g.,10, 20, 30… or 01, 02, 03…………).

- Redundant zeros must be written.

- Numbering need not be continuous (i.e., sequence of 05, 10, 17, 55, etc. shall be acceptable).

- The direction of numbering coincides as a rule with that of fluid flow.

- Numbering conventions, once established, may not be altered, not even in the event of changes made in the progress of planning

- Equipment Unit Classification (A1, A2)

Equipment identification code is classification of mechanical, electrical and control and instrumentation equipment as per KKS Key. It forms the first part of Equipment unit code. See “Table-2”

Table-2

Few General defined Examples of Equipment Unit Classification Code (A1A2)

| A | Mechanical Equipment |
| --- | --- |
| AA | Valves, Dampers, etc. incl., actuators; AISO Manual |
| AB | Isolating elements, air locks |
| AC | Heat exchangers |
| AE | Turning, driving, lifting and slewing gear (incl. manipulators) |
| B | Mechanical Equipment |
| BB | Vessels, storage equipment’s (tanks) |
| BE | Shafts (for erection and maintenance only) |
| BF | Foundations |
| BG | Boiler heating surfaces |
| BN | Jet pumps, ejectors, injectors |
| BP | Flow restrictors and limiters (incl. rupture discs), orifices (not metering orifices) |
| BQ | Hangers, supports, frames, racks, pipe penetrations |
| BR | Piping, ductwork, chutes |
| C | Direct Measuring Circuits |
| CD | Density |
| CE | Electrical variables |
| CF | Flow, rate |
| CG | Distance, length, position, direction of rotation |
| CK | Time |
| CL | Level (also for dividing line) |
| CM | Moisture, humidity |
| CP | Pressure, Differential Pressure |
| CQ | Quality variables (analysis, pH, material properties) other than *CD*, *CM*, *CV* |
| CR | Radiation variables |
| CS | Velocity, speed, frequency(mechanical) |
| CT | Temperature |
| CU | Combined variables |
| CV | Viscosity |
| CW | Weight, mass |
| CX | Neutron flux (reactor power) |
| CY | Vibration, expansion, acceleration |
| G | Electrical & Instrumentation Equipment |
| GA | Analog Junction boxes |
| GB | Binary Junction boxes |
| GC | RTD Junction boxes |

- Equipment Unit Numbering (AN)

Equipment unit numbering is numbering of the mechanical, electrical and control and instrumentation equipment and forms the second part of Equipment unit code.

Equipment numbering will be single stepped as 001, 002, …, 999 and according to numbering of piping, valve and measuring circuit.

- See Table 3 for numbering of valves

- See Table 4 for numbering of Instruments.

| Table 3 (Numbering of Valves) |  |  |
| --- | --- | --- |
| Sequence / Range From | Sequence / Range up to | Type of valve |
| 001 | 099 | Motorized Actuated on-off Valves |
| 100 | 299 | Pneumatic Actuated on-off Valves |
| 300 | 399 | Control Valves |
| 400 | 499 | Safety Valves |
| 500 | 599 | Check Valves |
| 600 | 999 | Manual Valves |

| Table 4 (Numbering of Instruments) |  |
| --- | --- |
| Sequential Number Range | Measuring Circuits |
| 001 – 099 | Primary Elements i.e., FE, AE, TE, VE, WE |
| 101 – 199 | Process Transmitters i.e., DT, FT, LT, PT, AT, ST, TT, WT, VT, pHT, DPT |
| 201 – 299 | Process Switches (Blind) i.e., FS, LS, PS, TS, VS, DPS |
| 301 – 399 | Not Used |
| 401 – 499 | Test Measurements i.e., PP, TW |
| 501 – 699 | Local Indicators / Gauges / Process indicator with Contact i.e., FI, LI, PI, AI, TI, VI, FG, LG, PG, TG, DPI, DPG, FIS, LIS, PIS, TIS, VIS, DPIS |
| 701 – 899 | Not Used |
| 901 – 999 | Derived signals (e.g., median, average) |

- Component Classification (B1, B2, BN)

Component classification is the classification of signals or signal applications as per KKS Key and forms the first part of Component code. The “process-related identification” of the plant coding system forms the base of the classification and identification of signal.

The following signals will be identified:

- Every signal that requires the planning of the electrical wiring and thus the entire interface signals with the terminal board;

- All the information that will be displayed to the operator by the advanced interface operator;

- All the information from/to other control system (local package) by communication link.

See “TABLE-5” for Mechanical & Electrical component codes.

Mechanical & Electrical component codes (TABLE - 5)

| Electrical Components |  |
| --- | --- |
| A | Assemblies and subassemblies |
| B | Transducers for non-electrical to electrical variables and vice-versa |
| C | Capacitors |
| D | Binary elements, delay devices, memory devices |
| E | Special components |
| F | Protective devices |
| G | Generators, power supplies |
| H | Signaling devices |
| K | Relays, contactors |
| L | Inductors |
| M | Motors |
| N | Amplifiers, controllers |
| P | Measuring instruments, testing equipment |
| Q | Power switchgear |
| R | Resistors |
| S | Switches, selectors |
| T | Transformers |
| U | Modulators, convertors from electrical to other electrical variables |
| V | Tubes, semiconductors |
| W | Transmission paths, waveguides, aerials |
| X | Terminals, plugs, sockets |
| Y | Electrical positioner, e.g. solenoids (not motors) |
| Z | Terminations, balancing equipment, filters, limiters, cable terminations, equalizers, hybrid transformers |
| K | Mechanical Components |
| KA | Gate valves, globe valves, dampers, cocks, rupture disks, orifices |
| KB | Gates, doors, damboards |
| KC | Heat exchangers, coolers |
| KD | Vessels/ tanks, pools, surge tanks (fluid systems) |
| KE | Turning, driving, lifting and slewing gear |
| KF | Continuous conveyors, feeders |
| KJ | Size reduction machines |
| KK | Compacting, packaging machines |
| KM | Mixers, agitators |
| KN | Compressors, blowers, fans |
| KP | Pumps |
| KT | Cleaning machines, dryers, separators, filters |
| KV | Burners, grates |
| KW | Stationary tooling and treatment machines for maintenance |
| M | Mechanical Components |
| MB | Brakes |
| MF | Foundations |
| MG | Gearboxes |
| MK | Clutches, couplings |
| MM | Engines, not electrical |
| MR | Piping components, ductwork components |
| MS | Positioners, not electrical |
| MT | Turbines |
| MU | Transmission gear, non-electrical, converters and boosters other than couplings and gearboxes |

  - Signal Designation

For B1 B2

- B1 shall be

X for Input Signal, Signal Origins

Y for Output Signal, Signal Applications

- B2 shall be

A for Functional group control / sub-group control

B for Control interface

G for Binary process signals

Q for Analog signals

- BN = N1 N2 is the serial number and shall be used in conjunction with B2 as per Table-I

- Table-II

- Table-III & IV

Table I : For B2 = A “for Functional group control / sub-group control”

| Signal Description | B2 N1 N2 |
| --- | --- |
| Auto | A01 |
| Manual | A02 |
| Group Start | A03 |
| Group Stop | A04 |

Table II : For B2 = B “for Control interface”

| Signal Description | B2 N 1 N2 |
| --- | --- |
| Open, Start, Run, On | B01 |
| Close, Stop, Off | B02 |
| Free for use | B03 |
| Free for use | B04 |
| Forward Start | B05 |
| Reverse Start | B06 |
| Trip | B07 |
| Ready, Healthy | B08 |
| Unhealthy, Disturbance | B09 |
| Start/ Open/ On Permissive | B10 |
| Stop/ Close/ Off Permissive | B11 |
| Fault / Failure | B12 |
| Alarm / Trouble | B13 |
| Stand-by | B14 |
| Test | B15 |
| Local | B16 |
| Remote | B17 |
| Emergency Stop PB | B18 |
| Free for use | B19-B20 |
| Fuse Fail | B21 |
| Auto Change-over successful | B22 |
| Auto Change-over fail | B23 |
| Auto transfer inhibited | B24 |
| Under Voltage | B25 |
| Tap changing in process | B26 |
| Earth Fault | B27 |
| Protection Operated | B28 |
| REF Protection Operated | B29 |
| Under Voltage Trip | B30 |
| DC Supply-1 fail | B31 |
| DC Supply-2 fail | B32 |
| AC Supply fail | B33 |
| Buccholz Trip | B34 |
| Tap Position Discrepancy Operated | B35 |
| Pole Discrepancy Operated | B36 |
| Differential Protection Operated | B37 |
| Device Operated | B38 |
| Overall Differential | B39 |
| OLTC Stuckup | B40 |
| Low DC Volt | B41 |
| High DC Volt | B42 |
| On Bypass | B43 |
| Tap Changer Raise | B44 |
| Tap Changer Lower | B45 |
| MW Raise | B46 |
| MW Lower | B47 |
| Minimum Position | B48 |
| Maximum Position | B49 |
| Not Run, Not On, Not Open | B50 |
| Not Stop, Not Off, Not Closed | B51 |
| Free for use | B61~B99 |

Table III : For B2 = G “for Binary process signals”

| Signal Description | B2 N1 N2 |
| --- | --- |
| High / Activated | G01 |
| Low | G02 |
| HH (High High) | G03 |
| LL (Low Low) | G04 |
| HHH (High High High) | G05 |
| LLL (Low Low Low) | G06 |

Table IV : B2 = Q “for Analog signals”

| Signal Description | B2 N1 N2 |
| --- | --- |
| For Analog Signal status / Modulating Command (For Example: Transmitter / Command to CV) | Q01 |
| Current R Phase | Q05 |
| Current Y Phase | Q06 |
| Current B Phase | Q07 |
| Voltage R Phase | Q08 |
| Voltage Y Phase | Q09 |
| Voltage B Phase | Q10 |
| Active Power (W) | Q14 |
| Reactive Power (VAR) | Q15 |
| Active Energy (WH) | Q16 |
| Reactive Energy (VARH) | Q17 |
| Power factor | Q18 |
| Frequency | Q19 |
| Speed | Q20 |
| Apparent Power (MVA) | Q21 |
| Free for use | Q31~Q99 |

  - Signal Tagging Philosophy for Panel to Panel Interface I/Os:

For Panel to Panel Interface IOs, the IO tag number shall be

ZZZZZZZ-B1 B2 N1 N2 where

- ZZZZZZZ is the Panel Tag number

- B1 B2 is the signal type with respect to Control system and shall be

      - XH for Binary Input signals

      - YH for Binary Output signals

      - XJ for Analog Input signals

      - YJ for Analog Output signals &

- N1 N2 is the serial number (The serial number shall be sequential as indicated in the below example)

Wherever signal interface with DCS is envisaged, the Panel tag number shall be with respect to system code indicated in third party control system (PLC/microprocessor based) panel number. The same system code shall be used in tag number of both systems (DCS & third-party control system).

- EQUIPMENT TAGGING

The following describes the tagging systems and nomenclature to be used for equipment tagging. Plant equipment is segregated into three distinct categories:

- Mechanical Equipment, Valves & Specialties

- Electrical Equipment

- Instrument and Control Equipment

The three categories use a similar naming convention, but there are differences as outlined below.

  - Mechanical Equipment, Valves, Pumps & Instrument

The format for mechanical equipment tag numbering shall consist of the following:

UU-FFF-SS-DD-NNN

UU	Plant Code, For RNSG we use 50

FFF	System Code (TABLE - 1), Example For RNSG, “HTA10” is described as Flue Gas Ducting

SS	System Numbering Code (Designer to put the number as per direction of flow/ Sides).

DD	Equipment Unit Code (Table - 7)

NNN	Equipment Number

Numbering logic to be used for numbering of Valves is indicated in the Table-3

- Electrical Equipment

The format for Electrical equipment tag numbering shall consist of the following:

UUFFFNN

UU	Plant Code

FFF	System Code (Table - 1)

NN	Equipment Number (01 - 99)

E.g. MV Transformer for FGD will be tagged as 50BBT01.

All motors shall be tagged with the same equipment number as the driven equipment (i.e. fan, pump, compressor, etc.) with component code (i.e. “M”) as suffix. Local Push button stations of motors shall have tag no. same as that of the corresponding driven equipment with “PB” as suffix.

  - Instrument and Control Equipment:

- Instruments

The format for instrument and control equipment tag numbering shall consist of the following:

UUFFFSSDDNNN

UU	Plant Code

FFF	System Code

SS	System Numbering Code

DD	Instrument Type Code (Table-7)

NNN	Instrument Sequential Number (Table-4)

Notes:

- ‘UUFFSS shall be same as the parent pipe / equipment on which the instrument is mounted.

- Sequence number for derived signal shall be such that the last digit is similar to the first Instrument tag sequence number.

E.g. Median signal tag number of triple redundant pressure transmitters 50LCA01CP101, 50LCA01CP102 & 50LCA01CP103 shall be 50LCA01CP901; similarly, for 50LCA01CP104, 50LCA01CP105 & 50LCA01CP106, it shall be 50LCA01CP904.

Additional Codes:

- Valve/Damper related accessories, i.e. Position Feedback Switches/Transmitters, Positioners etc. shall be tagged based on the Valve/Damper tag number.

- For position feedback instrument tagging, equipment code AA of corresponding Valve tag number shall be replaced by CG

- Junction Box (JB), Instrument Racks (LIE/LIR) & Local Control Panel (LCP) Numbering

UUFFFSSDDNNN

UU			Plant Code

F1 F2 F3	System Code-(System code shall be ‘HTY’= Control and protection equipment)

S1 S2			System Numbering Code

S1 S2 shall be subdivision of the System (F1 F2 F3) as defined in Table-V

D1 D2 			Equipment Type Code (Table-VI)

N1 N2 N3 		Sequential Number (001 - 999)

Table-V

|  | S1 S2 | Sub-system Description |
| --- | --- | --- |
| For Smartluth use only | 01-05 | FGTR Area |
|  | 06 | Boost-Up Fan Area |
|  | 07 | MCU Area |
|  | 08 | Wet Stack Area |
|  | 09 | SAC Plant Area |
|  | 10-50 | Reserved for future use |
| For Packages | 51 | Boost-Up Fans |
|  | 52 | Blowers |
|  | 53 | Dampers |
|  | 54 | Expansion Joints |
|  | 55 | Pumps |
|  | 56 | FGTR |
|  | 61 | MCU |
|  | 62 | Wet Stack |
|  | 63 | HVAC |
|  | 64 | Fire Detection System |
|  | 65 | Fire Protection System |
|  | 66 | Compressed Air System |
|  | 67 | Neutralization System |
|  | 68 | Zero Liquid Discharge Plant |
|  | 69 | Reserved for future use |
|  | 70 | Reserved for future use |
|  | 71 | Reserved for future use |
|  | 72 | Reserved for future use |
|  | 73 | Reserved for future use |

Table VI

| D1D2 | Description |
| --- | --- |
| GA | Analog Junction Box |
| GB | Digital Junction Box |
| GC | RTD Junction Box |
| GD | Thermocouple Junction Box |
| GE | SOV Junction Box |
| GG | Foundation fieldbus Junction box |
| GJ | PA Junction box (Process Automation) |
| GK | DP Junction box (Decentralized Peripherals) |
| GV | Vibration Junction Box |
| GZ | Instrument Racks (LIE / LIR) |
| GH | Local control panel |
| GK | Local information display unit |
| GQ | Electrical Junction Box |

E.g., Tag number for Boost-Up Fan JB/Rack shall be:

Analog JB:				50HTY51GA001

Digital JB:				50HTY51GB001

RTD JB:				50HTY51GC001

TC JB:				50HTY51GD001

SOV JB:				50HTY51GE001

Inst. Rack:				50HTY51GZ001

Vibration JB:				50HTY51GV001

Foundation Fieldbus JB:		50HTY51GG001

PA JB:				50HTY51GJ001

DP JB:				50HTY51GK001

Local Control Panel:		50HTY51GH001

- Instrument & Control Panel (Other than Local Control Panel) Numbering

The format for instrument & control panel numbering shall consist of the following:

UUFFFNN

UU	Plant Code

F1 F2 F3	System Code

- For  F1F2 shall indicate the type of Panel as per Table VII

- F3 shall be ‘H’ for FGD and ‘G’ for SAC

NN	Panel Number (00-99)

Table VII

| F1 F2 | Description |
| --- | --- |
| CA | Cabinets for Protective interlocks |
| CJ | Unit Coordination level |
| CM | Vibration Monitoring System |
| CN | Remote I/O Cabinet |
| CQ | Relay Cabinet |
| CR | Process Control System (DCS – System Cabinets) |
| CS | Network (Switch) cabinet |
| CT | Power Distribution cabinet |
| CV | Marshalling Racks |
| CW | Control Room Equipments e.g. Workstation, Server, printers, LVS etc |
| CY | Communication and information system |
| CZ | Others |

Few Examples of Equipment Code Classification (B1 B2)

| Equipment Codes (For This Project)- TABLE: 7 |  |
| --- | --- |
| AA= Valves | GE= POWER CABLES |
| AD= Spray nozzles for FGTR & MCU | GF= Electrical/Control Cables and Glands |
| AE= Lifting device | GH= LTMCC/SWITCHBOARD |
| AN= Booster Fan | GK= PLC |
| AP= Pump | GS= SWITCHGEAR |
| AQ= Damper | GW= Electrical Panels and Junction Boxes |
| AT= Filtering unit | GX= PMCC, MCC, ACDB and DCDB |
| AY= Expansion joints | KA= Lighting material |
| BB= Tanks | KP=Grounding Material |
| BQ= Hanger/ SUPPORTS/ STEEL STRUCTURES | MA= MOTORS |
| BR= Piping/ Duct | MD= MOV |
| BU= Insulation / Sheathing | PA= Painting/Primer |
| BY= Slider bearing | UC= CIVIL Materials |
| GC= CONTROL CABLE | YA= Air Conditioning/HVAC |
| GD= CABLE TRAY | YY= Glass flake lining/ LINING |

Mechanical Equipment, Valves, Pumps & Instrument

The format for mechanical equipment tag numbering shall consist of the following:

Rev-2

UU-FFF-SS-DD-NNN

UU	Plant Code, For RNSG we use 50

FFF	System Code (TABLE - 1), Example For RNSG, “HTA10” is described as Flue Gas Ducting

Rev-3- Position Changed

SS	System Numbering Code (Designer to put the number as per direction of flow/ Sides).

DD	Equipment Unit Code (Table - 4)

NNN	Equipment Number

Tagging/ Numbering logic is indicated below:

      - OTHER TAGGING

- Cable Numbering

- Electrical Cable Numbering

The format for cable numbering shall consist of the following:

UUFFFNNSYYYZ

UUFFFNN	From Equipment No

S		Segregation Code (1 to 4)

= 1 For MV Power Cable

= 2 For LV Power Cable

= 3 For Control Cable

= 4 For Instrumentation Cable

YYY		Serial number 001-999

Z		Cable suffix: A, B, C…..Z,AA,AB,..BA,…ZZ

For example,

Cable numbers for HT switchgear incomer may read as 50BBA01 1 001 A..etc.

- Instrumentation Cable Numbering

- Junction Box Multicables

Tag number for multicables from Junction Boxes, shall be derived from the corresponding Junction Box Tag number, replacing equipment code GA/ GB/ GC/ GD/ GE/ GG /GJ / GK / GZ as per TABLE-VIII and prefixed with “_”

Table VIII

| Description | Suitable for GA/ GB/ GC/ GD/ GE/ GG /GJ / GK / GZ | Remarks |
| --- | --- | --- |
| For Multicable from SOV JB (GE) | 11 – 19 | If SOV voltage is AC |
|  | 21 – 29 | If SOV voltage is > 60 V DC |
|  | 31 – 39 | If SOV voltage is < 60 V DC |
| For Multicable from Analog JB (GA) | 41 – 49 |  |
| For Multicable from Digital JB (GB) | 51 – 59 |  |
| For Multicable from RTD JB (GC) | 61 – 69 |  |
| For Multicable from Thermocouple JB (GD) | 71 – 79 |  |
| For Multicable from Vibration JB (GV) | 81 – 89 |  |
| For Multicable from Foundation fieldbus JB (GG) | G1 – G9 |  |
| For Multicable from PA fieldbus JB (GJ) | J1 – J9 |  |
| For Multicable from DP fieldbus JB (GK) | K1 - K9 |  |

- Analog Cable

Multipair Cable Number from Analog JB 50HTY01GA051 shall be:

1st cable – 50HTY01_41051

2nd cable – 50HTY01_42051

- Digital Cable

Multipair / Multicore Cable Number from Digital JB 50HTY01GB051shall be:

1st cable – 50HTY01_51051

2nd cable – 50HTY01_52051

- Foundation Fieldbus cables

Main Cable Number from Foundation Fieldbus JB 50HTY01GG001 shall be

1st cable – 50HTY01_G1001

2nd cable – 50HTY01_G2001

- PA Fieldbus cables

Main Cable Number from Profibus PA Fieldbus JB 50HTY01GJ001 shall be

1st cable – 50HTY01_J1001

2nd cable – 50HTY01_J2001

- DP Fieldbus cables

Main Cable Number from Profibus DP Fieldbus JB 50HTY01GK001 shall be

1st cable – 50HTY01_K1001

2nd cable – 50HTY01_K2001

- Panel to Panel Cables

Panel to Panel Cable numbers shall initiate with Source panel tag number, followed by Destination panel tag number & Cable serial number (N1N2N3), where

N1 = 	0 for Power Cable,

1 for Foundation Fieldbus cable

2 for PA cable

3 for DP cable

4 for Analog cable,

5 for Digital cable

6 for RTD cable

7 for Thermocouple cable &

9 for Communication cable

And N2N3 shall be the serial number

E.g., Tag number of Analog Cable between Panels ‘50CMH01’ & ‘50CVH01’ shall be 50CMH01_50CVH01_401

- Branch / Direct Cables

Branch cables tag number shall be a combination of the corresponding Instrument & Junction box serial number joined by “_”

E.g., Branch Cable number of Ultrasonic Level 50HTA01CL101 wired to Analog JB 50HTY06GA321 shall be 50HTA01CL101_321

Similarly, Direct cable tag numbers shall be a combination of the corresponding Instrument & Panel serial number joined by “_”

E.g. Cable tag number for direct cable from Instrument 50HTA01CL102 to Panel 50CVH01 shall be 50HTA01CL102_01

    - Cable Raceway Numbering

    - Cable trays

The format for cable tray numbering shall consist of the following:

UUNNGGNA

UU			Plant Code (50 for Unit 5)

NN	Area Code = For FGD Bldg. Ground Floor "F0", For FGD Bldg. First Floor "F1"..

For SAC Bldg. Ground Floor "G0", For FGD Bldg. First Floor "G1"..

GG	Sequential Numbering (01,02,03…)

N	Raceway Segregation

Segregation Code (N):

= M, for medium voltage cable (33 kV, 11 kV, 6.6 kV, 3.3 kV)

= L, for low voltage cable (1.1 kV, 600 V, 240V, 220V, etc.)

= C, for control cables (1.1kV)

= K, for instrumentation cables 600V Paired Cables Fire protection cables, communication cables and Fiber optic cables

A	Numbering Subdivision (1,2,3…)

1 = First layer (Top) layer of tray of same segregation

2 = Second layer of tray of same segregation

3 = Third layer of tray of same segregation

    - Conduit

UUAASNNNNZ

UU	Unit code (50 for Unit 5)

AA	Conduit Type

EC = Embedded Conduit

HP= Hume Pipe

C = Above Ground Conduit

S	Segregation (M, L, C, K)

= M, for medium voltage

= L, for low voltage

= C, for control

= K, for instrumentation

NNNN	sequential number, 0001 to 9999

A	Sequential numbering of layer of same conduit segregation (A, B, C, D…)

    - Manhole/Doors

UU-MH-NNNN

UU = Unit code (50 for Unit 5)

MH = Manhole

NNNN = sequential number of manhole, 0001 to 999

| FFF-SS | AT A GLANCE TO UNDERSTOOD (KKS SYSTEM CODE) |
| --- | --- |
|  | HTA- Flue gas ducting system |
|  | HTA10- Flue gas ducting TO EXISTING CHIMNEY RHS |
|  | HTA20- Flue gas ducting TO EXISTING CHIMNEY LHS |
|  | HTA11- Flue gas ducting tap-off to FGD INLET LHS |
|  | HTA22- Flue gas ducting tap-off to FGD INLET RHS |
|  | HTA30- Flue gas ducting COMMON INLET TO BOOSTER FAN |
|  | HTA40- Flue gas ducting OUTLET FROM BOOSTER FAN TO MCU |

| DD | KKS COMPONENT CODE: |
| --- | --- |
|  | AQ- DAMPERS |
|  | AY- EXPANSION JOINTS |
|  | CT- TEMPERATURE TRANSMITTER (101 TO 999) |
|  | CP- PRESSURE INDICATOR LOCAL (501-699) |
|  | CP- PRESSURE TRANSMITTER (101-199) |
|  | AA- MANUAL VALVE (001 TO 099) |
|  | AA- MOTORISED VALVE (600-999) |

Plant Equipment Tagging Examples

Valves

Manual isolation valve (Flue Gas Line)

50HTA10AA600

Rev-2

Equipment’s

50PBLXX-AP001

Pump

PT

50HTA11CP101

Instruments:

Pressure Transmitter