## Tr-9
Comment Resolution Sheet (CRS)
Plant | Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant
Project | Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System
Contract | HIL/RPD/FGD#5/ON SHORE/01 Dated 01/Nov/2021
Transmittal No. | G21001/TR/0009 |  | Dated | 2022-01-04
HIL Comment |  | W L Gore Remark | B&V Comments |  | W L Gore Remark
Drawing /Document No. | Comment |  | Drawing /Document No. | Comment
3-1.SPC_Pumps. | MOC of pump is not mentioned in the datasheet | Vendor To Specify Recirculation Pump will be PFA lined with mechanical seals | RPDU5.PG.301 | The scope defined in section (A.General and D. Scope of Services ), add training of personnel for operation and maintenance of offered equipment | To be agreed by Vendor
| Pump head, capacity to be provided. | Vendor To Specify |  | In Codes and Standards, indicate "Hydraulic Insitute", also electrical standards like IEEE, IEC which are applicable | Noted
| Motor specifications for all the 6 Pumps need to be provided | Vendor To Specify |  | Is Safety shower and eyewash supply included in this package or will be procured in separate package? | Not in scope of SAC Vendor
| Ash content in the Diluted acid need to be considered, if any | Already Included in Specification |  | In ANNEXURE -1 – TECHNICAL DATASHEET, the design, manufacture and testing codes and standards are not indicated for all equipment and tank. | Vendor to specify
| Desired Pump Curve to be provided | At contract stage, by Vendor. |  | In ANNEXURE -1 – TECHNICAL DATASHEET, the water quality of makeup available at site can be provided. The design site condition for cooling tower is not indicated. | Will be incorporated.
| Consider Sufficient margin over design flow and frictional head for Pumps and design the motors accordingly | Vendor to specify as per process requirement. |  | In ANNEXURE -1 – TECHNICAL DATASHEET, provide piping and valve material for any waste water handling. | Vendor to specify
ANNEXURE -1 – TECHNICAL DATASHEET | We urgently need information regarding total utility requirements(Tentative): 1. Chilled Water 2. Cooling Water 3. Instrument Air | Tentetive figure will be provided at proposal stage. |  | SECTION – 2 – SPECIFCATION OF TANKS- This section does not indicate the requirement to be fulfilled for FRP tank like construction and design standard and other technical requirements. The spec only talks about welding of CS tanks and other technical requirements pertaining to CS tanks. | Vendor will advice.
| Acid Neutralising Pit Description as per requirement | Not Required. |  | Annexure-S2-1 does not indicate the testing requirement of each tank and testing standard to be used. The design and construction standard for FRP tank is not indicated. | Vendor will advice.
| You mentioned that Supplier to estimate total steam. But, as the PRDS has already been designed on the basis of details mentioned in the Contract. | PRDS finalization to be done after offer received from vendor |  | SECTION – 3 – SPECIFCATION OF PUMPS- Include O&M Manual in Scope of Services | To be provided during Contract stage by Vendor
| Please again clearly mention the Pipeline/Valves MOC. Its confusing | Please see revised Spec. |  | 7.Annexure-6-Post Order Deliverable List does not indicate Technical datasheets, performance curves and layout drawings for equipment. It also does not include submission of shop test reports. | Will be incorporated.
| Please provide separate Scope of Civil Work under Renusagar team. Like Pathway, Drainage, Platform/Ladder for making approach | Civil scope is not a part of this spec. Vendor will only provide equipment loads and platforms loads |  | 1.S21001-TS01-05GNE-997201-R0- c. Scope of supply , and supervision of erection and commissioning : Please include the followings also in scope of supply/services: a) Raceway system including cable trays, conduits, support, steel structure etc. b) any modification required in the existing electrical system including metering/protection, raceway, steel support, panel extension, panel additional, power, control, instrument, special cables, terminations, harware etc. | Noted
| How many HMI panels will be needed, both Main and remote. | At the local point control there will be one HMI and one engineering station. |  | 3.Annexure-2 - Electrical standard SPEC: DATA SHEET FOR ELECTRICAL MOTOR A. POWER SUPPLY REQUIRED Supply Description Consumer L.T. Supply 415V, 3 Phase, 4W, 50 Hz, effectively earthed. - Motors upto 160KW H.T. Supply 6.6 kV, 3 Phase, 3W, 50 Hz, Non-effectively earthed. - Motors above 160 kW 415 V power supply shall be used up to 200 kW motors and above 200 kW 6.6 kV power supply shall be used. | Noted, HT supply not applicable.
| How are you going to Control ash Content in the Dilute Acid entering SAC to 50 PPM. What if it increases. Consider additional Ash Filters, if | 10 PPM |  | 1.03.0 Lamps All fixtures shall have lamps installed therein by the Contractor. All lamps shall be LED type or fluorescent as required for each unit. All lighting can be proposed to be LED type only. | Noted
STANDARD ELECTRICAL SPECIFICATIONS | Danger and instruction plates as per IS-2555 and in compliance with I.E. Rules. It should be IS-2551 | Noted |  | All low voltage motors shall be as energy efficient motors IE class 3 for continuous duty and IE2 for intermittent duty. | Vendor to comply.
| Construction of all panel should be IP 42 instead of proposed IP 3X. | Noted |  | Cables shall be provided with fire resistant coating rated for at least for 60 min for entry/exit/vertical runs/horizontal runs per applicable codes/practices. | Noted
| All junction boxes , conduits flexible conduits should be corrosion resistant for Sulphuric acid. | Noted |  | All cables shall be provided with FRLS low smoke zero halogen type construction. | Noted
| Motor weighing 25 kg. or more shall be provided with eye bolt or other adequate provision of lifting. All motor should be provided with eye bolt | Noted
| Motor including fan shall be painted with corrosion proof paints with colour shade 631 of IS-5. Guarantee of life at least 5 year of these paint coating should be specified. | Noted, vendor to specify based on industrial practice.
STANDARD ELECTRICAL SPECIFICATIONS: P12 | LT Power supply supply: it should be 3W instead of 4W | Noted
| HT power supply should also be effectively earthed | Not Applicable
| HT Motor > 200 kW | Not Applicable
| PERMISSIBLE VOLTAGE AND FREQUENCY VARIATION: Design the system without DC Power for SAC plant. | Noted
STANDARD ELECTRICAL SPECIFICATIONS: Section- E3: 2.05 and 2.06 | All LV (Power, lighting and control) cable should be of copper and 1100V instead of 650 V throughout the project and conform to IS 694. | Lighting is not is SAC vendor scope.
| Cables greater than 16 sq mm should be proposed to Aluminium. | Noted
s