## Table 1
COMMENT RESOLUTION SHEET
B&V Project No:
Owner: Hindalco Industries Limited (HIL); Consultant: Black & Veatch (B&V) |  | Project Name: HIL RENUSAGAR
Drawing No: |  | S21001-EN01-05HSD-221027 / RPDU5.ML.000 -R-0 (SHT 1 OF 1)
Drawing Revision No: |  | 0
Drawing Title: |  | FGD - General Arrangement Drawing (OVERALL PLOT PLAN)
1
Sr No | HIL /B&V Comments 10/01/2022 | Gore's Reply
1 | PLEASE DIFFERENTIAITE BETWEEN EXISTING AND NEW FACILITIES FOR CLARITY IN PDF. | NOTED. SHALL BE DIFFERENTIATED IN REVISED DRAWING
2 | PLEASE INCLUDE ELECTRICAL ROOM, EQUIPMENT, FACILITIES LOCATION IN THIS LAYOUT. | A SEPARATE ADDITIONAL FLOOR OF EXISTING ELECTRICAL BUILDING SHALL BE CONSTRUCTED BY HIL AND THE SAME FLOOR WILL BE USED FOR ELECTRICAL ROOM OF THE FGD PLANT. EXISTING ELECTRICAL ROOM WILL BE MARKED IN THE PLOT PLAN
3 | PLEASE PROVIDE REFERENCE FOR RACEWAY SYSTEM THROUGH CABLE TRAY, CONDUITS, TRENCH ETC. | A SEPARATE DRAWING OF CABLE RACEWAY, TRAY /CONDUITS LAYING WILL BE MADE
4 | PLEASE PROVIDE REFERENCE FOR ELECTRICAL INTERFACE POINTS WITH THE EXISTING ELECTRICAL SYSTEM, GROUNDING, LIGHTING, LIGHTNING PROTECTION ETC. (AS APPLICABLE). | GROUNDING , ILLUMINATION AND LIGHTNING PROTECTION IF ANY SHALL HAVE THEIR SEPARATE LAYOUT DRAWING
5 | PLEASE INCLUDE REFERENCE DRAWINGS FOR ELECTRICAL ROOM ELEVATION DETAILS. | ELECTRICAL EQUIPMENT LAYOUT DRAWING WILL BE SHOWN IN REVISED DRAWING
6 | PLEASE CONFIRM THAT THERE IS NO INTERFERENCE WITH THE EXISTING ELECTRICAL FACILITIES INCLUDING UNDERGROUND UTILITIES AND NEW SYSTEM WILL BE DESIGNED TAKING THAT INTO ACCOUNT WITHOUT AFFECTING THE EXISTING FACILITIES/SYSTEM. | ABOVE GROUND ROUTING OF ELECTRICAL SYSTEM WILL NOT HAVE ANY INTERFERENCE WITH THE EXISTING FACILITIES; HOWEVER, FOR ANY UNDERGROUND AND /OR TRENCH ROUTING, EXISTING UNDERGROUND FACILITY SHALL BE RELOCATED BY HIL.
7 | ANY MODIFICATIONS IN EXISTING ELECTRICAL SYSTEM TO FACILITATE SUPPLY TO NEW SYSTEM SHALL ALSO BE IN CONTRACTOR SCOPE INCLUDING PANEL ADDITIONS, BUS EXTENSIONS, STEEL SUPPORTS, METERING AND PROTECTION, CABLING (POWER/CONTROL/SIGNAL/SPECIAL CABLES), RACEWAY, RACEWAY SUPPORT, HARDWARE, STEEL SUPPORTS, HVAC ETC. (AS APLLICABLE). | THIS PART IS SCOPE RELATED AND THE SCOPE WILL BE AS PER CONTRACT
8 | Typical comment for all new facilities: Indicate distance of each new structure, building or equipment from the existing facility and equipment | NOTED. REFERENCE DISTANCE FROM EXISTING FACILTY SHALL BE GIVEN TO FGTR AND THEREAFTER ALL OTHER NEW ITEMS /FACUILITY WILL BE DIMENSIONED FROM FGTR
9 | Indicate Northing and Easting Co-ordinate of the Wet Stack Centreline | NOTED. SHALL BE SHOWN ON RECEIPT OF SAME.
10 | Show the sectional views A-A and B-B as indicated in the GA drawing | NOTED. SECTION A-A IS UNDER PREPARATION AND WILL BE ISSUED SHORTLY IN REVISED DRAWING.
11 | Show Maintenance space for Booster Fan | IT WILL BE SHOWN IN THE BOOSTER FAN GA DRAWING. BOOSTER FAN GA DRAWING SHALL BE MADE AFTER RECEIPT OF DIMENSIONAL GENERAL ARRANGEMENT DRAWING OF BOOSTER FAN FROM THE PROSPECTIVE SUPPLIER
12 | Provide description for the abbreviated names of equipment and vessels (PWT, FWT etc) | NOTED. SHALL BE INDICATED
13 | Confirm and indicate the following equipment are shown below FGTR Hopper on this GA drawing: 1) FGD Process Recycle Pumps 2) FGD Hopper cleaning pumps 3) FGD Wash recycle pumps 4) FGD Process Water Pumps | CONFIRMED. SAME WILL BE IDENTIFIED
14 | Show all equipment within the Acid Plant Area | IT IS THE GENEREL ARRANGEMENT /LAYOUT DRAWING OF ACID PLANT AND WILL BE DEVELOPED BY ACID PLANT SUPPLIER
15 | Requirement of hard stand for crane and movement of crane should be shown | NOTED. SAME SHALL BE MARKED BASED ON CONSTRUCTION METHODOLOGY OF FGTR ETC
16 | Show location of CEMS along with control panel on GA drawing | NOTED. SHALL BE INDICATED
17 | Please incorporate the storm water drainage requirement in the layout and its connection with the existing/outfall point. | SEPARATE DRAINAGE SYSTEM DRAWING WILL BE MADE TO SHOW IT
18 | Please provide the Construction laydown requirements as developed and identified | TO BE PROVIDED LATER AFTER UNANIMOUS DECISION OF CONSTRUCTION METHODOLOGY
19 | Please verify minimum road width, utility rack height, utility rack width, bridge height and bridge width (width defined as clearance between supports has been considered as per Statutory requirement. | IN THE PLOT PLAN , ROAD WILL BE SHOWN. REQUIREMENT OF RACK IS STILL UNDER STUDY. IF RACK IS PROVIDED, NECESSARY ELEVATION SHOWING CLEARANCE AND HEAD ROOM FROM THE ROAD ETC SHALL BE SHOWN.
20 | Please include the new roads connecting to the existing plant roads to each new facilities. | SEE ABOVE
21 | Topographical information contour elevation and Wind Rose developed and verified with client should be included | THE SAME HAS BEEN JUST RECEIVED. THE INFORMATION WILL BE AVAILABLE IN SUBSEQUENT SUBMISSION.
22 | Please include Coordinate system for site tied into the world/governmental vertical and horizontal datum as per client's requirement. | ELEVATION ABOVE MSL, RL ETC SHALL BE INDICATED IN REVISED DRAWING
23 | Chemical/fuel, etc. deliveries to made onsite during operation evaluated and verified and accordingly proper clearances are considered in the layout design. | COMMENT IS NOT UNDERSTOOD. PLEASE ELABORATE
24 | Crane access corridors required during construction to be shown on the layout drawing | THIS ASPECT WILL BE REVIEWED JOINTLY WITH HIL AND CRANE APPROACH TO ERECTION SITE WILL BE MARKED
25 | Please provide the paving areas as required for vehicular and non vehicular access. | NOTED
26 | Please include all the necessary UG utility pipes connections for new facilities. | NOT YET ENVISAGED
27 | Show truck/tanker access where acid is stored and needs to be transported | NOTED
28 | Show cable trays / pipe racks | STILL UNDER CONSIDERATION WHETHER RACK OR TRENCH SYSTEM WILL BE PROVIDED.
29 | Add a table with all facilities | DETAILED REQUIREMENT MAY PLEASE BE INDICATED.
30 | Show all legends and add a table with all legends | NOTED
31 | Total area requirement for SDFGD system not mentioned in the layout plan | THE SAME MAY BE SEEN IN THE PLOT. IN A BROWNFIELD SUCH MARKING IS DIFFICULT.
32 | Show MSL. Also, add: all levels are absolute levels with respect to the mean sea level | NOTED AS RESPONDED EARLIER
33 | Latitude and longitude are not marked in the plant layout preparation | NOTED. SHALL BE MARKED FOR A KEY POINT
34 | Finished ground floor level shall be EL 0.0 corresponding to RL.. | NOTED . SHALL BE INDICATED AS STATED EARLIER
35 | Existing facilities-both underground and over ground water and electrical lines shall be superimposed in the layout plan as well as show the clash points | SUGGEST ALL EXISTING UNDERGROUND FACILITIES BE RELOCATED TO AVOID ANY SURPRISE IN FUTURE.
36 | Electrical power connection not marked in the layout plan | IT WILL BE SHOWN IN THE ELECTRICAL EQUIPMENT LAYOUT PLAN
37 | All Terminal points (TPs) needs to be shown. | NOTED
38 | Colour legends to be mentioned. | NOTED
39 | All equipment and buildings are to be marked and tabulated. | ALREADY MARKED AND TABULATION SHALL BE DONE
40 | Road bend radius to be mentioned. | SHALL BE INDICATED WHEN THE ROADS WILL BE SHOWN
41 | Two wheelers & four wheelers parking space for employees to be shown. | TO BE DISCUSSED WITH HIL AND THE AREA /SPACE SHALL BE MARKED
42 | Site office construction area to be marked. | TO BE DISCUSSED WITH HIL AND THE AREA /SPACE SHALL BE MARKED
43 | Fire fighting system including hydrant, monitor etc. to be shown in red colour. This is required for statutory clearance from Factory Directorate. | SEPARATE LAYOUT OF FIRE FIGHTING SYSTEM SHALL BE DRAWN SHOWING THE REQUIRED EQUIPMENT
HIL's General Comment Please add the safety in the design of all equipment and their foundation from starting itself so that nothing to be done later for making platform, access etc at the time of PSSR. Hence please review and consider the safety parameters in each engineering.---- NOTED