|  |  | Owner: HINDALCO INDUSTRIES LIMITED Ahura Centre, 1st Floor, B Wing, Mahakali Caves Road, Andheri (East), Mumbai - 400 093, India |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | EPCM Contractor: W. L. GORE & ASSOCIATES (Pacific) Pte, Ltd. India Branch 703, A-Wing, 215 Atrium, Andheri Kurla Road, Mumbai 400059, India |  |  |  |  |  |
|  |  | Nominated Subcontractor - Engineering, Quality Control, Supervision: SMARTLuth Solution and Service Pvt. Ltd. Unit No: 503, 5th Floor, ECO Centre,. EM-4 Sector-V, Salt Lake City, Kolkata - 700091, India |  |  |  |  |  |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System FGD – Process DBR Design Basis Report ` ISSUED FOR; APPROVAL; INFORMATION; MANUFACTURING; CONSTRUCTION; AS-BUILT. |
| 0 | 21-02-2022 | First Submission | IR | IR |  | BCB |  |
| Rev. | Date | Description of revision | Prepared | Checked |  | Approved |  |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant |  |  | Drg. / Doc. No.: S21001- EN01- 05CPP- 221038 |  |  |  |  |
| Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System |  |  | Gore Doc. No.: RPDU5.PG.500 |  |  |  |  |
| FGD - Process DBR Design Basis Report |  |  | GORE Job No.: RPDU5 |  |  |  | Rev. : 0 |
|  |  |  | File: FGD Process DBR Design Basis |  |  |  |  |
| This document is a property of W.L. GORE & ASSOCIATES (Pacific) Pte, Ltd. and it may contain trade secrets or privileged, undisclosed or otherwise confidential information. If you have received this document in error, you are hereby notified that any review, copying or distribution of it is strictly prohibited. |  |  |  |  |  |  |  |

FGD PROCESS DESIGN BASIS

The total flue gases from the 80 MWe boiler unit will be treated in the FGD System with adequate controls and protections. The control philosophy will cover the entire load range between 60% to 100% TMCR, generally operated with no oil support.

The existing 80 MWe boiler has 2 x 60 % duty ID fans handling the flue gas of the boiler and discharging independently to a stack. The FGD process will tap off the flue gas with a maximum volumetric flow rate of 586,669 Am3/Hr(wet) at an average temperature of 148 degC maximum

from the individual discharge duct of the ID fans leading to the stack, retrofitting new ducts with the necessary isolation damper at the take off point to the FGD and a new isolation damper retrofitted on the existing ductwork to the stack at the downstream of the FGD take off point. The two individual-off take ducts will form into a common suction header carrying the total flue gas volume, for the 1 x 100% duty Booster Fan with double suction entries. The flow control of the booster fan will be achieved by fan speed control using a variable frequency drive.

The centrifugal booster fan of the unit will discharge the total flue gas to the Mist Cooling Unit (MCU) where the flue gas will be conditioned by spray water cooling to a saturation point with Relative Humidity close to 100% saturation. The gas temperature at the outlet is expected to be at circa 53 °C after the Mist Cooling Unit.

Softened raw water of adequate purity, low in chlorides, from the station will be used as the Process Water for Mist Cooling. The process water make-up (23.56 m3/hr) is stored in the Process Water Tank from where 2 x 100% Process Water Pumps feed the in-duct spray nozzle grid of the MCU to spray water in a mist form for evaporative heat exchange of the flue gas, thereby reducing the flue gas temperature and attaining saturated condition. An amount of excess process water collected at the bottom of the MCU hoppers will be collected in a pit where it will be neutralised by an alkali dosing system. The neutralised water in the pit will be sent for use to the station’s boiler bottom ash handling system via 2 x 100% Waste Water sump pumps. The same sump pumps will also be used intermittently for jetting the MCU hoppers to maintain a clean outflow channel. Recovered water(4.48 m3/hr) from the SAC plant is also returned back to the process water tank to supplement the make up to the system.

An emergency head tank of 5 m3 volume is provided to spray water into the MCU via separate spray nozzles during loss of power supply when all auxiliaries trip and while the booster fan coasts down until the station emergency board is restored to ensure that the catalyst modules are protected against high temperature. The Emergency Head Tank is always kept filled from the Process Water Pump discharge header.

The balance of the make up water(2.43 m3/hr) is fed through a separate Fresh Water Tank and 2 x 100% duty Fresh Water Pumps which feeds the intermittent water requirement of Mist Eliminator washing, Acid Transfer Filter back washing and fresh water make up to the FGTR hopper to maintain acid concentration of 10% in the 9 off FGTR hoppers.

After the Mist Cooling Unit (MCU), the saturated flue gas will enter the Reactor Tower via flow streamliners for SOx capture. The Flue Gas Treatment Reactor (FGTR) is stacked with layers of GoreTM  SPC catalyst modules arranged in 165 stacks with a maximum of 22 vertical layers (inclusive of 5 of catalyst management layers), arranged with a maximum of 5 vertical layers per stack in series , for SOx capture with sufficient space for future addition of layers. The gas velocity through the modules will be designed to a maximum of 2.2 mtr/ sec.

The surface of the SPC modules is kept clean by an automated water washing and misting system, using the dilute acid in the 9 off FGTR hoppers. The 2 x 100% duty Wash Recycle Pumps keep the modules clean. The recirculating wash water flow of 46.46 m3/hr will be feeding washing and misting nozzles located at various elevations inside the FGTR. 15 vertical washing zones have been created to sequentially wash the modules in a cycle which can be continued in a loop.

After the flue gas flows through all the layers of the FGTR modules, it passes through a Mist Eliminator at the top to remove water droplets entrained in the flue gas. The surface of the Mist Eliminator is kept clean by an intermittent wash, using fresh softened water, fed via the Fresh Water Pumping System.

The treated flue gas leaves the FGTR and the Mist Eliminator at the top via transition piece and expansion joint to the atmosphere at circa 56 mtr height via a wet stack mounted on steel structures at the top of the FGTR.

The 10% dilute sulfuric acid collected at the bottom of the FGTR is pumped by 2 x 100% Acid Transfer Pumps to the SAC plant via 2 x 100% duty Transfer Acid Filters. The transferred acid (4.78 m3/hr) is stored in Dilute Acid Storage tank in the SAC Plant area of adequate holding capacity. The acid concentration in the hoppers of the FGTR is controlled and maintained by the addition of softened fresh water from the Fresh Water Pumping System from time to time. The Transfer Acid Ash Filters are kept clean by back washing using Fresh Water from the Fresh Water Pumping System. The back washed water is sent to the Neutralising Pit for further discharge to the stations bottom ash system. The same 2 x 100 % Acid Transfer Pump system is used to keep the FGTR hopper outflow channels clean by intermittent jetting.

The 10% dilute acid from the Dilute Acid Storage tank is pumped by 2 x 100% duty pumps for the acid concentration process. The acid is concentrated to circa 70 in the first stage through a multi evaporative process. The 70% acid then serves as the feed to the second stage of single stage evaporation to concentrate the acid to 95%.  The achieved final acid concentration of 95% is stored in the Concentrated Acid Tank for onward transportation to end users using 2 x 100% duty Conc. Acid Loading Pumps.

2 x 100% duty Conc. Acid Recirculation pumps are provided to recirculate the initially concentrated acid in the Concentrated Acid Storage Tank back to the Dilute Acid Storage Tank for plant start up until the H2SO4 concentration in the Dilute Acid Storage tank is greater than 8%.

The recovered water from the SAC process is stored in the Recovered Water Storage Tank and sent back at the rate of 4.48 m3/hr to the Process Water Tank to supplement the process make up via 2 x 100% duty Recovered Water Pumps.

The SAC plant requires low grade auxiliary steam from the boilers and Cooling Water from the station for the process. The heating steam condensate is returned back to the DM Plant.

The system has been designed keeping in mind the reliability, availability and maintainability.