## ITP - Flue Gas Dampers
|  |  |  | INSPECTION AND TEST PLAN . |  |  |  | Client Doc. No. S21001- IT01- 05CPP- 664046
|  |  |  | For: Non-Metallic Expansion Joint |  |  |  | Gore Doc. No. |  | Rev. 00
| Plant: | Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant - Flue Gas Desulfurization Project with GORETM SPC technology | [5 empty] | File:
| Supplier: |  | Order No: |  | P.T.S. No: |  |  |  | ITEM No.
POS. |  | INSPECTIONS AND TESTS |  | PROCEDURES | CODES & | 1) | QUALITY SURVEILLANCE - % OF INSPECTION
|  |  |  | DRAWINGS - D/S | STANDARDS |  | SUPPLIER | GORE | HINDALCO |  | NOTE
INTERMEDIATE INSPECTIONS
|  | Pre Fabbrication Meeting (PFM) |  |  |  |  | H | H |  |  | PFM Report
I. | 10 | Order, drawings, procedures, specifications, WPS, |  | Order
PQR, document list and ITP review.
[6 empty] | YES | H | R |  |  | 100%
I. | 20 | Material certificate review |  | See Drawing List
[6 empty] | YES | H | R |  |  | 100%
I. | 30 | Welding documents rewiev (WPS/PQR/WQ) |  |  | EN 15614 or
ASME IX
|  | LP or MT on 30% of welds |  |  | DIN EN 571-1 | YES | H | W
ASME V
I. | 40
|  | Visual inspection of welds, fabric with metal joints |  |  |  | YES | H | W |  |  | 100%
I. | 50
FINAL INSPECTIONS
|  | Visual and dimensional inspection |  | drawing |  | YES | H | W |  |  | 100%
F. | 10
|  | Tightness, leak check or depressurization |  |  |  | YES | H | W |  |  | 100%
F. | 20 |  |  | approved supplier procedure
|  | Painting inspection |  |  |  | YES | H | W |  |  | 100%
F. | 30 |  |  | painting procedure
|  | Final inspection before shipment |  |  |  |  | H | H | R
|  | - QC certificates review |  | Order
F. | 40 | - Completeness of the supply
|  | - Issue of FIR |  |  |  | YES
LIST OF APPLICABLE DRAWINGS:
SUPPLIER DRAWING
1) R=Documents review W=Witness point H=Hold Point YES=Certificate required FIR=Final Inspection Report TPI=Third Party Inspection Agency