## TANKS & VESSELS (hidden)
| TAG NO. | EQUIPMENT NAME | CAPACITY | QTY | SHELL VOLUME | DIA | HEIGHT | SHELL THK | DISH/END PL. THK. | JACKET THK. | TANK WT. | NOZZLES WT. | LUGS WT. | JACKET WT. | cone sm. Dia | cone BOTM. st. ht | cone I/M. Dia | cone TOP st. ht | cone volume |  | TORISPHERICAL HEAD VOLUME | TOTAL TANK VOLUME | actual vol reqd | shell vol. reqd. | straight ht reqd | extra ht provided | FREE BOARD provided | VACANT SHEEL
TANKS
10 | T-102 | DIGESTED SLURRY FLASH TANK | CAP.-26 M3 | 1 | 25.7519 | 2.7 | 4.5 | 6 | 8 | 2.5
14 | T-105 | SODIUM SILICATE TANK | CAP.- 25 M3 | 1 | 25.7519 | 2.7 | 4.5 | 6 | 8
36 | T-107 | SODIUM CARBONATE TANK | CAP.- 25 M3 | 1 | 25.7519 | 2.7 | 4.5 | 6 | 8
51 | T-101 | CAUSTIC LYE STORAGE TANK | CAP.- 25 M3 | 1 | 25.7519 | 2.7 | 4.5 | 6 | 8
53 | T-103 | CAUSTIC DILUTION TANK | CAP.- 20 M3 | 1 | 22.0781 | 2.5 | 4.5 | 6 | 8
65 | T-106 | FEED WATER TANK | CAP.- 20 M3 | 1 | 22.0781 | 2.5 | 4.5 | 6 | 8
67 | T-110 | RO WATER STORAGE TANK | CAP.- 18 M3 | 1 | 22.0781 | 2.5 | 4.5 | 6 | 8
59 | T-104 | RAW WATER TANK | XXXX | 1 | 3.2311 | 1.4 | 2.1 | 6 | 8
61 | T-108 | CONC. H2SO4 TANK | CAP.-3 M3 | 1 | 3.5325 | 1.5 | 2 | 6 | 8
63 | T-109 | DIL. H2SO4 TANK | CAP.-3 M3 | 1 | 3.5325 | 1.5 | 2 | 6 | 8
VESSELS
7 | AMV-101 | ASH MIXING VESSEL | CAP.- 25 M3 | 1 | 25.7519 | 2.7 | 4.5 | 6 | 8 | 2.5 | [6 empty] | 0.3 | 0.6 | 1.4568 |  | 1.9119 | 29.1206
9 | PD-101 | PRESSURE DIGESTER | CAP.-25 M3, dT-90-170°C | 1 | 25.7519 | 2.7 | 4.5 | 6 | 8 | 2.5
19 | PR-101 | PRECIPITATOR | CAP.-22 M3, | 1 | 22.0781 | 2.5 | 4.5 | 6 | 8 | 2.5 | [6 empty] | 0.3 | 0.6 | 1.2745 |  | 1.533 | 24.8856
23 | V-101 | SILICA CAKE LIQUIFICATION VESSEL-1 | CAP.- 12 M3 | 1 | 12.4579 | 2.3 | 3 | 6 | 8 | 2.5 | [6 empty] | 0.3 | 0.6 | 1.1048 |  | 1.2077 | 14.7704
26 | V-102 | SILICA CAKE LIQUIFICATION VESSEL-2 | CAP.- 20 M3 | 1 | 22.0781 | 2.5 | 4.5 | 6 | 8 | 2.5
29 | V-103 | SILICA CAKE LIQUIFICATION VESSEL-3 | CAP.- 12 M3 | 1 | 12.4579 | 2.3 | 3 | 6 | 8 | 2.5
39 | RE-101 | REGENERATOR UNIT | CAP.-25 M3 | 1 | 25.7519 | 2.7 | 4.5 | 6 | 8 | 2.5
44 | V-105 | CaCO3 LIQUIFICATION VESSEL | CAP.-3 M3 | 1 | 3.5325 | 1.5 | 2 | 6 | 8 | 2.5 | [6 empty] | 0.3 | 0.6 | 0.5516 |  | 0.3605 | 4.4446
VESSELS EFFECTIVE VOLUME
| AMV-101 | ASH MIXING VESSEL | CAP.- 25 M3 | 1 | 22.8906 | 2.7 | 4 |  | 5.7227 | [7 empty] | 1.7 | 0.25 | 1.8354 |  | 1.9119 | 26.6379 | 17.78 | 15.9446 | 2.7862 | 1.2138
| PD-101 | PRESSURE DIGESTER | CAP.-25 M3, dT-90-170°C | 1
| PR-101 | PRECIPITATOR | CAP.-22 M3, | 1 | 22.0781 | 2.5 | 4.5 |  | 4.9062 | [7 empty] | 1.587 | 0.25 | 1.5885 |  | 1.533 | 25.1996
| V-101 | SILICA CAKE LIQUIFICATION VESSEL-1 | CAP.- 12 M3 | 1 | 11.8351 | 2.3 | 2.85 |  | 4.1526 | [7 empty] | 1.467 | 0.25 | 1.3519 |  | 1.2077 | 14.3947 | 8.3 | 6.9481 | 1.6732 | 1.1768 | 4.887 | 0.6229 | 0.15
| V-102 | SILICA CAKE LIQUIFICATION VESSEL-2 | CAP.- 20 M3 | 1 | 21.3422 | 2.5 | 4.35 |  | 4.9062 | [7 empty] | 1.467 | 0.25 | 1.4532 |  | 1.533 | 24.3284 | 16.34 | 14.8868 | 3.0343 | 1.3157 | 6.4554 | 0.73594 | 0.15
| V-103 | SILICA CAKE LIQUIFICATION VESSEL-3 | CAP.- 12 M3 | 1 | 11.8351 | 2.3 | 2.85 |  | 4.1526 | [7 empty] | 1.467 | 0.25 | 1.3519 |  | 1.2077 | 14.3947 | 8.49 | 7.1381 | 1.7189 | 1.1311 | 4.697 | 0.6229 | 0.15
| RE-101 | REGENERATOR UNIT | CAP.-25 M3 | 1 | 22.8906 | 2.7 | 4 | [15 empty] | 17.44 | 17.44 | 3.0475 | 0.95246
| V-105 | CaCO3 LIQUIFICATION VESSEL | CAP.-3 M3 | 1 | 3.2676 | 1.5 | 1.85 |  | 1.7663 | [7 empty] | 1 | 0.25 | 0.60568 |  | 0.3605 | 4.2337 | 1.44 | 0.83432 | 0.47237 | 1.3776 | 2.4332 | 0.26494 | 0.15
TANKS
| T-105 | SODIUM SILICATE TANK | CAP.- 25 M3 | 1 | 24.8935 | 2.7 | 4.35 | [9 empty] | 1 | 0.25 | 1.0928 |  | 1.9119 | 27.8983 | 17.86 | 16.7672 | 2.93 | 1.42 | 8.1264 | 0.8584 | 0.15
| T-107 | SODIUM CARBONATE TANK | CAP.- 25 M3 | 1 | 24.8935 | 2.7 | 4.35 | [9 empty] | 1 | 0.25 | 1.0928 |  | 1.9119 | 27.8983 | 17.44 | 16.3472 | 2.8566 | 1.4934 | 8.5464 | 0.8584 | 0.15
| T-101 | CAUSTIC LYE STORAGE TANK | CAP.- 25 M3 | 1 | 24.8935 | 2.7 | 4.35 | [9 empty] | 1 | 0.25 | 1.0928 |  | 1.9119 | 27.8983 | 3.45 | 2.3572 | 0.4119 | 3.9381 | 22.5364 | 0.8584 | 0.15
| T-103 | CAUSTIC DILUTION TANK | CAP.- 20 M3 | 1 | 21.3422 | 2.5 | 4.35 | [9 empty] | 1.467 | 0.25 | 1.4532 |  | 1.533 | 24.3284 | 17.78 | 16.3268 | 3.3278 | 1.0222 | 5.0154 | 0.73594 | 0.15
| T-110 | RO WATER STORAGE TANK | CAP.- 18 M3 | 1 | 21.3422 | 2.5 | 4.35 | [9 empty] | 1 | 0.25 | 0.99856 |  | 0.3605 | 22.7012 |  | -0.99856 | -0.20353 | 4.5535
| T-108 | CONC. H2SO4 TANK | CAP.-3 M3 | 1 | 3.2676 | 1.5 | 1.85 | [9 empty] | 1 | 0.25 | 0.60568 |  | 0.3605 | 4.2337 |  | -0.60568 | -0.34292 | 2.1929
| T-109 | DIL. H2SO4 TANK | CAP.-3 M3 | 1 | 3.2676 | 1.5 | 1.85 | [9 empty] | 1 | 0.25 | 0.60568 |  | 0.3605 | 4.2337 | 0.02 | -0.58568 | -0.3316 | 2.1816
| VESSELS EFFECTIVE VOLUME | [17 empty] | (DEAD VOLUME) | STORAGE
| RE-101A/B | REGENERATOR UNIT | CAP.-43 M3 | 2 | 37.312 | 3.25 | 4.5 | [7 empty] | 0.3 | 0.5 | 1.769 | 0.4 | 0.4911 | 2.0368 | 2.105 | 41.9449 | 18.41
| DG-01/DG-02 | DIGESTOR | CAP.-45 M3, dT-90-170°C | 2 | 21.195 | 3 | 3 | [7 empty] | 0.3 | 0.35 | 1.876 | 0.25 | 0.38247 | 1.1883 | 2.5688 | 25.3345 | 21.5
| PR-101A/B | PRECIPITATOR | CAP.-40 M3, | 2 | 18.4632 | 2.8 | 3 |  | 6.1544 | [5 empty] | 0.3 | 0.35 | 1.769 | 0.25 | 0.34377 | 1.0426 | 2.105 | 21.9546 | 17.61
| V-101 | SILICA CAKE LIQUIFICATION VESSEL-1 | CAP.- 42 M3 | 1 | 9.42 | 2 | 3 |  | 3.14 | [5 empty] | 0.3 | 0.35 | 1.292 | 0.25 | 0.1968 | 0.54042 | 0.803 | 10.9602 | 8.3
| V-103A/B | SILICA CAKE LIQUIFICATION VESSEL-3 | CAP.- 42 M3 | 2 | 9.42 | 2 | 3 | [7 empty] | 0.3 | 0.35 | 1.292 | 0.25 | 0.1968 | 0.54042 | 0.803 | 10.9602 | 8.49
| V-102 | SILICA CAKE LIQUIFICATION VESSEL-2 | CAP.- 73 M3 | 1 | 18.4632 | 2.8 | 3 |  | 6.1544 | [5 empty] | 0.3 | 0.35 | 1.769 | 0.25 | 0.34377 | 1.0426 | 2.105 | 21.9546 | 16.34
| V-105 | CaCO3 LIQUIFICATION VESSEL | CAP.-6 M3 | 1 | 1.6956 | 1.2 | 1.5 |  | 1.1304 | [5 empty] | 0.3 | 0.35 | 0.825 | 0.25 | 0.093332 | 0.20368 | 0.1915 | 2.1841 | 1.44
TANKS
| T-105 | SODIUM SILICATE TANK | CAP.- 80 M3 | 1 | 18.4632 | 2.8 | 3 | [7 empty] | 0.3 | 0.35 | 1.769 | 0.25 | 0.34377 | 1.0426 | 2.105 | 21.9546 | 17.86
| T-107 | SODIUM CARBONATE TANK | CAP.- 80 M3 | 1 | 18.4632 | 2.8 | 3 | [7 empty] | 0.3 | 0.35 | 1.769 | 0.25 | 0.34377 | 1.0426 | 2.105 | 21.9546 | 17.44
| T-101 | CAUSTIC LYE STORAGE TANK | CAP.- 25 M3 | 1 | 18.4632 | 2.8 | 3 | [7 empty] | 0.3 | 0.35 | 1.769 | 0.25 | 0.34377 | 1.0426 | 2.105 | 21.9546 | ??(tanker size)
| T-103 | CAUSTIC DILUTION TANK | CAP.- 73 M3 | 1 | 18.4632 | 2.8 | 3 | [7 empty] | 0.3 | 0.35 | 1.769 | 0.25 | 0.34377 | 1.0426 | 2.105 | 21.9546 | 17.78
| T-108 | CONC. H2SO4 TANK | CAP.-5 M3 | 1 | 2.6494 | 1.5 | 1.5 | [7 empty] | 0.3 | 0.35 | 1 | 0.25 | 0.12742 | 0.31103 | 0.3564 | 3.4442
| T-109 | DIL. H2SO4 TANK | CAP.-5 M3 | 1 | 2.6494 | 1.5 | 1.5 | [7 empty] | 0.3 | 0.35 | 1 | 0.25 | 0.12742 | 0.31103 | 0.3564 | 3.4442
| T-106 | FEED WATER TANK | CAP.- XX M3 | 1
| T-110 | FILTERED WATER TANK | CAP.- 22 M3 | 1
| T-114A/B/C/D | DRINKING WATER TANK | CAP.-1.0 M3 | 4
| T-111A/B/C | SW & DW TANK | CAP.-2 M3/Hr. | 2
| T-112 | RO DISTRIBUTION TANK | CAP.-50 M3 | 1
| T-113A/B | RO WATER STORAGE TANK | CAP.- 130 M3 | 2
| T-104 | RAW WATER STORAGE TANK | CAP.-300 M3 | 1
#REF!
[7 empty] | 87.0551 | [8 empty] | 140.6006
| TAG NO. | EQUIPMENT NAME | CAPACITY | QTY
| AMV-101 | ASH MIXING VESSEL | CAP.- 29 M3 | 1
| RE-101 | REGENERATOR UNIT | CAP.-22 M3 | 1
| PD-101 | PRESSURE DIGESTER | CAP.-25 M3, dT-90-170°C | 1
| PR-101 | PRECIPITATOR | CAP.-22 M3, | 1
| V-101 | SILICA CAKE LIQUIFICATION VESSEL-1 | CAP.- 11 M3 | 1
| V-103 | SILICA CAKE LIQUIFICATION VESSEL-3 | CAP.- 11 M3 | 1
| V-102 | SILICA CAKE LIQUIFICATION VESSEL-2 | CAP.- 22 M3 | 1
| V-105 | CaCO3 LIQUIFICATION VESSEL | CAP.-2 M3 | 1
TANKS
| T-105 | SODIUM SILICATE TANK | CAP.- 22 M3 | 1
| T-107 | SODIUM CARBONATE TANK | CAP.- 22 M3 | 1
| T-101 | CAUSTIC LYE STORAGE TANK | CAP.- 22 M3 | 1
| T-103 | CAUSTIC DILUTION TANK | CAP.- 22 M3 | 1
| T-108 | CONC. H2SO4 TANK | CAP.-3 M3 | 1
| T-109 | DIL. H2SO4 TANK | CAP.-3 M3 | 1
| T-102 | DIGESTED SLURRY FLASH TANK | CAP.-24 M3, | 1
| T-106 | FEED WATER TANK | CAP.- XX M3 | 1
| T-110 | RO WATER STORAGE TANK | CAP.- 5 M3 | 1
| T-104 | RAW WATER STORAGE TANK | CAP.- 50 M3 | 1
| T-111 | SERVICE WATER TANK | CAP.-1 M3 | 1
| T-112 | DRINKING WATER TANK | CAP.-1 M3 | 1
| T-113 | RO WATER STORAGE TANK | CAP.- 50 M3 | 1

## TANKVESSEL WT. (hidden)
TAG NO. | EQUIPMENT NAME | CAPACITY(SELECTED) | QTY |  | MATERIAL | SHELL VOLUME | DIA | HEIGHT | cone sm. Dia | cone st. ht | SHELL THK | DISH/END PL. THK. | CONE THK. | JACKET THK. | MET. UNIT WT | SHEEL WT | DISHED END WT | CONE WT. | TANK WT. | NOZZLES WT. | LUGS WT. | JACKET SHELL WT. | JACKET CONE WT. | SUB TOTAL | MATERIAL
[6 empty] | IN M3 | IN MTR. | IN MTR. | IN MTR | IN MTR | IN MM | IN MM | IN MM | IN MM |  | IN KGS | IN KGS | IN KGS | IN KGS | IN KGS | IN KGS | IN KGS | IN KGS | IN KGS | MS | SS
VESSELS EFFECTIVE VOLUME | [26 empty] | 0
RE-101A/B | REGENERATOR UNIT | CAP.-43 M3 | 2 | WITH JACKET+INSULATION | SHELL-MS, JACKET-MS | 18.4632 | 2.8 | 3 | 0.3 | 0.35 | 6 | 8 | 6 | 3.15 | 7.85 | 1243.1009 | 62.8457 | 80.2325 | 1386.179 | 69.309 | 138.6179 | 676.1512 | 44.8396 | 2315.0967 | 2315.0967
DG-01/DG-02 | DIGESTOR | CAP.-45 M3, dT-90-170°C | 2 | WITH JACKET+INSULATION | SHELL-MS, JACKET-MS | 21.195 | 3 | 3 | 0.3 | 0.35 | 6 | 8 | 6 | 3.15 | 7.85 | 1331.8938 | 72.1442 | 85.4088 | 1489.4468 | 74.4723 | 148.9447 | 722.7824 | 47.5572 | 2483.2034 | 2483.2034
PR-101A/B | PRECIPITATOR | CAP.-40 M3, | 2 | WITH JACKET+INSULATION | SHELL-SS-304, JACKET-MS | 18.4632 | 2.8 | 3 | 0.3 | 0.35 | 6 | 8 | 6 | 3.15 | 7.85 | 1243.1009 | 62.8457 | 80.2325 | 1386.179 | 69.309 | 138.6179 | 676.1512 | 44.8396 | 2315.0967 | 720.9908 | 1594.1059
V-101 | SILICA CAKE LIQUIFICATION VESSEL-1 | CAP.- 42 M3 | 1 |  | SHELL-SS-304 | 9.42 | 2 | 3 | 0.3 | 0.35 | 6 | 8 | 6 | 0 | 7.85 | 887.9292 | 32.0641 | 59.5273 | 979.5206 | 48.976 | 97.9521 | 0 | 0 | 1126.4487 |  | 1126.4487
V-103 | SILICA CAKE LIQUIFICATION VESSEL-3 | CAP.- 42 M3 | 1 |  | SHELL-SS-304 | 9.42 | 2 | 3 | 0.3 | 0.35 | 6 | 8 | 6 | 0 | 7.85 | 887.9292 | 32.0641 | 59.5273 | 979.5206 | 48.976 | 97.9521 | 0 | 0 | 1126.4487 |  | 1126.4487
V-102 | SILICA CAKE LIQUIFICATION VESSEL-2 | CAP.- 73 M3 | 1 |  | SHELL-SS-304 | 18.4632 | 2.8 | 3 | 0.3 | 0.35 | 6 | 8 | 6 | 0 | 7.85 | 1243.1009 | 62.8457 | 80.2325 | 1386.179 | 69.309 | 138.6179 | 0 | 0 | 1594.1059 |  | 1594.1059
V-105 | CaCO3 LIQUIFICATION VESSEL | CAP.-6 M3 | 1 |  | SHELL-MS | 1.6956 | 1.2 | 1.5 | 0.3 | 0.35 | 6 | 8 | 6 | 0 | 7.85 | 266.3788 | 11.5431 | 38.8222 | 316.744 | 15.8372 | 31.6744 | 0 | 0 | 364.2556 | 364.2556
| TOTAL |  | 10
TANKS
T-105 | SODIUM SILICATE TANK | CAP.- 80 M3 | 1 | WITH JACKET+INSULATION | SHELL-SS-304, JACKET-MS | 18.4632 | 2.8 | 3 | 0.3 | 0.35 | 6 | 8 | 6 | 3.15 | 7.85 | 1243.1009 | 62.8457 | 80.2325 | 1386.179 | 69.309 | 138.6179 | 676.1512 | 44.8396 | 2315.0967 | 720.9908 | 1594.1059
T-107 | SODIUM CARBONATE TANK | CAP.- 80 M3 | 1 | WITH JACKET+INSULATION | SHELL-MS, JACKET-MS | 18.4632 | 2.8 | 3 | 0.3 | 0.35 | 6 | 8 | 6 | 3.15 | 7.85 | 1243.1009 | 62.8457 | 80.2325 | 1386.179 | 69.309 | 138.6179 | 676.1512 | 44.8396 | 2315.0967 | 2315.0967
T-101 | CAUSTIC LYE STORAGE TANK | CAP.- 25 M3 | 1 |  | SHELL-MS | 18.4632 | 2.8 | 3 | 0.3 | 0.35 | 6 | 8 | 6 | 0 | 7.85 | 1243.1009 | 62.8457 | 80.2325 | 1386.179 | 69.309 | 138.6179 | 0 | 0 | 1594.1059 | 1594.1059
T-103 | CAUSTIC DILUTION TANK | CAP.- 73 M3 | 1 |  | SHELL-SS-304 | 18.4632 | 2.8 | 3 | 0.3 | 0.35 | 6 | 8 | 6 | 0 | 7.85 | 1243.1009 | 62.8457 | 80.2325 | 1386.179 | 69.309 | 138.6179 | 0 | 0 | 1594.1059 |  | 1594.1059
T-108 | CONC. H2SO4 TANK | CAP.-5 M3 | 1 |  | SHELL-SS-304 | 2.6494 | 1.5 | 1.5 | 0.3 | 0.35 | 6 | 8 | 6 | 0 | 7.85 | 332.9735 | 18.0361 | 46.5866 | 397.5961 | 19.8798 | 39.7596 | 0 | 0 | 457.2355 |  | 457.2355
T-109 | DIL. H2SO4 TANK | CAP.-5 M3 | 1 |  | SHELL-SS-304 | 2.6494 | 1.5 | 1.5 | 0.3 | 0.35 | 6 | 8 | 6 | 0 | 7.85 | 332.9735 | 18.0361 | 46.5866 | 397.5961 | 19.8798 | 39.7596 | 0 | 0 | 457.2355 |  | 457.2355
T-106 | FEED WATER TANK | CAP.- XX M3 | 1
T-110 | FILTERED WATER TANK | CAP.- 30 M3 | 1
T-114A/B/C/D | DRINKING WATER TANK | CAP.-1.0 M3 | 4
T-111A/B/C | SW & DW TANK | CAP.-2 M3/Hr. | 2
T-112 | RO DISTRIBUTION TANK | CAP.-50 M3 | 1
T-113A/B | RO WATER STORAGE TANK | CAP.- 130 M3 | 2
T-104 | RAW WATER STORAGE TANK | CAP.-300 M3 | 1
| TOTAL |  | 18 | [21 empty] | 10513.74 | 9543.7921

## MEDIA (hidden)
SL. | MEDIA |  | MATERIAL | CLASS | SCH./THK | TYPE
1 | WET ASH
|  | VALVE/DAMPER | MS |  |  | KNIFE EDGE GATE
PIPE /DUCT
|  | TANK | MS
2 | DRY ASH
|  | VALVE/DAMPER | MS
|  | PIPE /DUCT | MS |  |  | CAST BASALT LINED
|  | TANK | MS
3 | ASH SLURRY
|  | VALVE/DAMPER | CI |  |  | GATE
|  | PIPE /DUCT | SS 304
|  | TANK | SS 304
4 | DIGESTED ASH SLURRY
|  | VALVE/DAMPER | CI |  |  | GATE/KNIFE EDGE GATE
|  | PIPE /DUCT | SS 304
|  | TANK | SS 304
5 | SODIUM SILICATE SLURRY
|  | VALVE/DAMPER | SS 304 |  |  | GATE
|  | PIPE /DUCT | SS 304
|  | TANK | SS 304
6 | Co2 GAS
|  | VALVE/DAMPER | MS |  |  | BALL
|  | PIPE /DUCT | CS
|  | TANK | MS
7 | SILICA SLURRY
|  | VALVE/DAMPER | SS 304 |  |  | GATE
|  | PIPE /DUCT | SS 304
|  | TANK | SS 304
8 | SODIUM CARBONATE
|  | VALVE/DAMPER | CS |  |  | GATE/GLOBE/NRV
|  | PIPE /DUCT | MS
|  | TANK | MS
9 | CALCIUM CARBONATE-DRY
|  | VALVE/DAMPER | MS
|  | PIPE /DUCT | MS
|  | TANK | MS
10 | CALCIUM CARBONATE-SLURRY
|  | VALVE/DAMPER | MS |  |  | GATE
|  | PIPE /DUCT | MS
|  | TANK | MS
11 | CAUSTIC- LYE
|  | VALVE/DAMPER | MS |  |  | GAGE/BALL
|  | PIPE /DUCT | MS
|  | TANK | MS
12 | CAUSTIC- DILUTED
|  | VALVE/DAMPER | SS 304
|  | PIPE /DUCT | SS 304
|  | TANK | SS 304
13 | Ca(OH)2 POWDER
|  | VALVE/DAMPER | MS
|  | PIPE /DUCT | MS
|  | TANK | MS
14 | RAW WATER
|  | VALVE/DAMPER | MS |  |  | GATE
|  | PIPE /DUCT | MS
|  | TANK | MS
15 | RO WATER
|  | VALVE/DAMPER | SS 304 |  |  | GLOBE
|  | PIPE /DUCT | SS 304
|  | TANK | SS 304
16 | H2SO4-CONC./DILUTED
|  | VALVE/DAMPER | SS 304/HESTALLOY |  |  | BALL
|  | PIPE /DUCT | SS 304/HESTALLOY
|  | TANK | SS 304/HESTALLOY
17 | STEAM / CONDENSATE
|  | VALVE/DAMPER | MS |  |  | GLOBE/GATE
|  | PIPE /DUCT | MS
|  | TANK | MS
18 | INSTRUMENT AIR
|  | VALVE/DAMPER | SS |  |  | BALL
|  | PIPE /DUCT | MS-GI
|  | TANK | SS
19 | COMPRESSED AIR
|  | VALVE/DAMPER | SS |  |  | BALL
|  | PIPE /DUCT | MS-GI
|  | TANK | MS-GI
20 | SERVICE WATER / DRINKING WATER
|  | VALVE/DAMPER | MS-GI |  |  | GATE
|  | PIPE /DUCT | MS-GI
|  | TANK | MS-GI
21 | DRY SILICA
|  | VALVE/DAMPER |  |  |  | KNIFE EDGE GATE
PIPE /DUCT
|  | TANK/HOPPER | SS 304
22 | DRY CaCo3
|  | VALVE/DAMPER | SS 304 |  |  | KNIFE EDGE GATE
|  | PIPE /DUCT | SS 304
|  | TANK | SS 304
23 | AIR- HOT / COLD
|  | VALVE/DAMPER | MS |  |  | BUTTERFLY/LOOVER
|  | PIPE /DUCT | MS
|  | TANK | MS
24
25
26
27
28
29
30
| ALL INST. ROOT VALVE |  |  |  |  | GATE
| EXCEPT FOR COMP. AIR & INST. AIR |  |  |  |  | BALL
| EXCEPT FOR WATER |  |  |  |  | GLOBE
| TANK DRAIN |  |  |  |  | GATE (LOCK CLOSED)
| DIRECT SOLENOID VALVE |  |  |  |  | UPTO 25 NB
| PNEU. OPRATED SOLENOID VALVE |  |  |  |  | ABOVE 25 NB
| SOCKET WELD |  |  |  |  | UPTO 50 NB
| FLANGED |  |  |  |  | ABOVE 50 NB

## DRIVE LIST (hidden)
DRIVE LIST FOR 5TPD SILICA PLANT FROM RICE HUSK ASH
| OWNER | UMZA INTERNATIONAL FARMS LTD |  | APPD./DT |  |  | DOC. NO. | BTIT-20TPD-SI-RFQ-13
| ENGINEER | BTIT ENGINEERING SOLUTION PVT. LTD. |  | CHD./DT |  |  | REF.
| EPC CONTRACTOR |  |  | MAKE/DT | 03.02.2020 |  | REV. | 0
SL. NO. | EQUIPMENT TAG NO. | DRG. REF. | D E S C R I P T I O N | WORKING/STAND-BY | DUTY | VOLTAGE | CONNECTION | MOTOR NAME PLATE RATING (KW) | MOTOR NAME PLATE RATING (HP) | CONSUMPTIVE LOAD (KW) | Quantity |  | REFERANCE |  | flow | head | density | eficiency | power | margin | selected motor
[11 empty] | Working | Standby |  |  | m3/hr | mwc | kg/m3 | in decimal | bkw | in decimal | kw
1 | CN-101 | BTIT/5TPD/PFD-001 (SHT-1 TO 6) | WET ASH CONVEYOR | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 0.75 | 1 | 0.37 | 1 |  | 01 NO. | CAP.-700 KG/HR.
2 | AD-101 | BTIT/5TPD/PFD-001 (SHT-1 TO 6) | ASH DRIER-1 | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 60 | 80 |  | 1 |  | 01 NO. | CAP.-500 KG/HR.
3 | CN-102 | BTIT/5TPD/PFD-001 (SHT-1 TO 6) | DRY ASH CONVEYOR | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 5.5 |  |  | 1 |  | 01 NO. | CAP.-500 KG/HR.
4 | CN-103 | BTIT/5TPD/PFD-001 (SHT-1 TO 6) | ASH FEED UNIT | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 3.75 |  |  | 1 |  | 01 NO. | CAP.-1800Kg/Hr
5 | AG-1 | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | AGITATOR FOR ASH MIXING VESSEL | WORKING | CONTINUOUS | 1-ph, 230 V AC | D O L | 11 | 15 | 11 | 1 |  | 01 NO.
6 | P-102A | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | ASH SLURRY TRANSFER PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 5.5 | 7.5 | 0.6875 | 1 |  | 01 NO. | CAP.-40 M3/Hr | 40 | 20 | 1030 | 0.7 | 3.2524 | 4.0655 | 5.5
7 | P-102B | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | ASH SLURRY TRANSFER PUMP | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 5.5 | 7.5 |  |  | 1 | 01 NO. | CAP.-40 M3/Hr | 40 | 20 | 1030 | 0.7 | 3.2524 | 4.0655 | 5.5
9 | AG-03 | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | AGITATOR FOR DIGESTED SLURRY FLASH TANK | WORKING | CONTINUOUS | 1-ph, 230 V AC | D O L | 2.2 | 3 | 0.275 | 1 |  | 01 NO.
10 | P-103A | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | FEED PUMP FOR ASH FILTER PRESS | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 15 | 20 | 1.875 | 1 |  | 01 NO. | CAP.- 40 M3/Hr | 40 | 60 | 1030 | 0.7 | 9.7572 | 12.1965 | 15
11 | P-103B | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | FEED PUMP FOR ASH FILTER PRESS | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 15 | 20 |  |  | 1 | 01 NO. | CAP.- 40 M3/Hr | 40 | 60 | 1030 | 0.7 | 9.7572 | 12.1965 | 15
12 | CN-104 | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | UNDIGESTED ASH CONVEYOR | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 3.75 |  |  | 1 |  | 01 NO. | CAP.- 1600 KG/HR
13 | F-101 | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | ASH FILTER PRESS | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 5.5 | 7.5 |  | 1 |  | 01 NO. | CAP.- 40 M3/Hr. | 40
14 | MIX-101 | BTIT/5TPD/PFD-001 (SHT-3 TO 6) | STATIC MIXER | WORKING | CONTINUOUS | 1-ph, 230 V AC | D O L | [5 empty] | 01 NO. | CAP.-40 M3/Hr.
15 | AG-04 | BTIT/5TPD/PFD-001 (SHT-3 TO 6) | AGITATOR FOR PRECIPITATOR | WORKING | CONTINUOUS | 1-ph, 230 V AC | D O L | 2.2 | 3 | 0.275 | 1 |  | 01 NO.
16 | EP-101 | BTIT/5TPD/PFD-001 (SHT-3 TO 6) | EJECTOR PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 15 |  |  | 1 |  | 01 NO. | CAP.- 90M3/Hr. | 90 | 50
17 | P-107A | BTIT/5TPD/PFD-001 (SHT-3 TO 6) | SILICA SLURRY PUMP-1 | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 15 | 20 | 1.875 | 1 |  | 01 NO. | CAP.- 40 M3/Hr, | 40 | 60 | 1030 | 0.7 | 9.7572 | 12.1965 | 15
18 | P-107B | BTIT/5TPD/PFD-001 (SHT-3 TO 6) | SILICA SLURRY PUMP-1 | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 15 | 20 |  |  | 1 | 01 NO. | CAP.- 40 M3/Hr, | 40 | 60 | 1030 | 0.7 | 9.7572 | 12.1965 | 15
19 | F-102 | BTIT/5TPD/PFD-001 (SHT-3 TO 6) | SILICA FILTER PRESS-1 | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 5.5 | 7.5 |  | 1 |  | 01 NO. | CAP.- 40 M3/Hr, | 40
20 | AG-06 | BTIT/5TPD/PFD-001 (SHT-3 TO 6) | AGITATOR FOR SILICA CAKE LIQUIFICATION VESSEL-1 | WORKING | CONTINUOUS | 1-ph, 230 V AC | D O L | 1.5 | 2 | 0.1875 | 1 |  | 01 NO.
21 | P-108A | BTIT/5TPD/PFD-001 (SHT-3 TO 6) | SILICA SLURRY PUMP-2 | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 15 | 20 | 1.875 | 1 |  | 01 NO. | CAP.-40 M3/Hr | 40 | 60 | 1030 | 0.7 | 9.7572 | 12.1965 | 15
22 | P-108B | BTIT/5TPD/PFD-001 (SHT-3 TO 6) | SILICA SLURRY PUMP-2 | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 15 | 20 |  |  | 1 | 01 NO. | CAP.-40 M3/Hr | 40 | 60 | 1030 | 0.7 | 9.7572 | 12.1965 | 15
23 | F-103 | BTIT/5TPD/PFD-001 (SHT-4 TO 6) | SILICA FILTER PRESS-2 | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 5.5 | 7.5 |  | 1 |  | 01 NO. | CAP.-40 M3/HR | 40
24 | P-110A | BTIT/5TPD/PFD-001 (SHT-4 TO 6) | SILICA SLURRY PUMP-3 | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 15 | 20 | 1.875 | 1 |  | 01 NO. | CAP.-40 M3/Hr | 40 | 60 | 1030 | 0.7 | 9.7572 | 12.1965 | 15
25 | P-110B | BTIT/5TPD/PFD-001 (SHT-4 TO 6) | SILICA SLURRY PUMP-3 | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 15 | 20 |  |  | 1 | 01 NO. | CAP.-40 M3/Hr | 40 | 60 | 1030 | 0.7 | 9.7572 | 12.1965 | 15
26 | F-104 | BTIT/5TPD/PFD-001 (SHT-4 TO 6) | SILICA FILTER PRESS-3 | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 5.5 | 7.5 |  | 1 |  | 01 NO. | CAP.-40 M3/Hr. | 40
27 | P-112A | BTIT/5TPD/PFD-001 (SHT-4 TO 6) | SILICA SLURRY PUMP-4 | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 3.7 | 5 | 0.4625 | 1 |  | 01 NO. | CAP.-40 M3/Hr | 40 | 15 | 1030 | 0.7 | 2.4393 | 3.0491 | 3.7
28 | P-112B | BTIT/5TPD/PFD-001 (SHT-4 TO 6) | SILICA SLURRY PUMP-4 | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 3.7 | 5 |  |  |  | 01 NO. | CAP.-40 M3/Hr | 40 | 15 | 1030 | 0.7 | 2.4393 | 3.0491 | 3.7
29 | D-101 | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | SILICA SPRAY DRIER UNIT | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 20 | 26.6667 |  | 1 |  | 01 NO. | CAP.-2400 KG/Hr
30 | CN-105 | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | PRODUCT SILICA CONVY. | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 5.5 |  |  | 1 |  | 01 NO. | CAP.-2400 KG/Hr
31 | AG-05 | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | AGITATOR FOR REGENERATOR | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 2.2 | 3 | 0.275 | 1 |  | 01 NO.
32 | CN-106 | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | Ca(OH)2 FEEDING UNIT | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 3.75 |  |  | 1 |  | 01 NO. | CAP.-900 KG/Hr
33 | P-115A | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | CaCO3 SLURRY PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 15 | 20 | 1.875 | 1 |  | 01 NO. | CAP.- 40 M3/Hr. | 40 | 60 | 1030 | 0.7 | 9.7572 | 12.1965 | 15
34 | P-115B | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | CaCO3 SLURRY PUMP | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 15 | 20 |  |  | 1 | 01 NO. | CAP.- 40 M3/Hr. | 40 | 60 | 1030 | 0.7 | 9.7572 | 12.1965 | 15
35 | F-105 | BTIT/5TPD/PFD-001 (SHT-6 TO 6) | CaCO3 FILTER PRESS-1 | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 5.5 |  |  | 1 |  | 01 NO. | CAP.-40 M3/Hr. | 40
36 | AG-09 | BTIT/5TPD/PFD-001 (SHT-6 TO 6) | AGITATOR FOR CaCO3 LIQUIFICATION VESSEL-2 | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 0.75 | 1 | 0.09375 | 1 |  | 01 NO. | CAP.-3 M3
37 | P-116A | BTIT/5TPD/PFD-001 (SHT-6 TO 6) | CaCO3 SLURRY PUMP-02 | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 2.2 | 3 | 0.275 | 1 |  | 01 NO. | CAP.-6 M3/Hr. | 6 | 40 | 1030 | 0.5 | 1.366 | 1.7075 | 2.2
38 | P-116B | BTIT/5TPD/PFD-001 (SHT-6 TO 6) | CaCO3 SLURRY PUMP-02 | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 2.2 | 3 |  |  | 1 | 01 NO. | CAP.-6 M3/Hr. | 6 | 40 | 1030 | 0.5 | 1.366 | 1.7075 | 2.2
39 | F-106 | BTIT/5TPD/PFD-001 (SHT-6 TO 6) | CaCO3 FILTER PRESS-2 | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 5.5 |  |  | 1 |  | 01 NO. | CAP.-6 M3/Hr. | 6
40 | CN-107 | BTIT/5TPD/PFD-001 (SHT-6 TO 6) | CaCO3 SPIN DRIER FEED CONVY. | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 3.75 |  |  | 1 |  | 01 NO. | CAP.-200 KG/Hr
41 | D-102 | BTIT/5TPD/PFD-001 (SHT-6 TO 6) | CaCO3 SPIN DRIER | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 15 |  |  | 1 |  | 01 NO. | CAP.-200 KG/Hr. FEED RATE:??
42 | CN-108 | BTIT/5TPD/PFD-001 (SHT-6 TO 6) | PRODUCT CaCO3 CONVY. | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 5.5 |  |  | 1 |  | 01 NO. | CAP.-200 KG/Hr
43 | P-101A | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | CAUSTIC LYE TRANSFER PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 0.55 | 0.75 | 0.06875 | 1 |  | 01 NO. | CAP.- 2 M3/Hr | 2 | 15 | 1000 | 0.5 | 0.16578 | 0.20722 | 0.55
44 | P-101B | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | CAUSTIC LYE TRANSFER PUMP | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 0.55 | 0.75 |  |  | 1 | 01 NO. | CAP.- 2 M3/Hr | 2 | 15 | 1000 | 0.5 | 0.16578 | 0.20722 | 0.55
45 | AG-10 | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | AGITATOR FOR CAUSTIC DILUTION TANK | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 2.2 | 3 | 0.275 | 1 |  | 01 NO.
46 | P-105A | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | DIL. CAUSTIC LYE TR. PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 2.2 | 3 | 0.275 | 1 |  | 01 NO. | CAP.- 20 M3/Hr | 20 | 20 | 1000 | 0.7 | 1.5788 | 1.9735 | 2.2
47 | P-105B | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | DIL. CAUSTIC LYE TR. PUMP | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 2.2 | 3 |  |  | 1 | 01 NO. | CAP.- 20 M3/Hr | 20 | 20 | 1000 | 0.7 | 1.5788 | 1.9735 | 2.2
48 | BLR-101(HOLD) | BTIT/5TPD/PFD-002 (SHT-2 TO 3) | STEAM BOILER | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 75 |  |  | 1 |  | 01 NO. | CAP.-5 TPH
49 | P-113A | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | CONC. H2SO4 TR. PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 0.55 | 0.75 | 0.06875 | 1 |  | 01 NO. | CAP.-2 M3/Hr | 2 | 10 | 1000 | 0.5 | 0.11052 | 0.13815 | 0.55
50 | P-113B | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | CONC. H2SO4 TR. PUMP | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 0.55 | 0.75 |  |  | 1 | 01 NO. | CAP.-2 M3/Hr | 2 | 10 | 1000 | 0.5 | 0.11052 | 0.13815 | 0.55
51 | AG-11 | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | AGITATOR FOR DIL. H2SO4 TANK | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 0.75 | 1 | 0.09375 | 1 |  | 01 NO.
52 | P-114A | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | DIL. H2SO4 TR. PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 0.55 | 0.75 | 0.06875 | 1 |  | 01 NO. | CAP.-2 M3/Hr | 2 | 10 | 1000 | 0.5 | 0.11052 | 0.13815 | 0.55
53 | P-114B | BTIT/5TPD/PFD-001 (SHT-5 TO 6) | DIL. H2SO4 TR. PUMP | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 0.55 | 0.75 |  |  | 1 | 01 NO. | CAP.-2 M3/Hr | 2 | 10 | 1000 | 0.5 | 0.11052 | 0.13815 | 0.55
54 | AG-02 | BTIT/5TPD/PFD-001 (SHT-2 TO 6) | AGITATOR FOR PRESSURE DIGESTOR VESSEL | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 2.2 | 3 | 0.275 | 1 |  | 01 NO.
55 | AG-07 | BTIT/5TPD/PFD-001 (SHT-4 TO 6) | AGITATOR FOR SILICA CAKE LIQUIFICATION VESSEL-2 | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 1.5 | 2 | 0.1875 | 1 |  | 01 NO.
56 | AG-08 | BTIT/5TPD/PFD-001 (SHT-4 TO 6) | AGITATOR FOR SILICA CAKE LIQUIFICATION VESSEL-3 | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 1.5 | 2 | 0.1875 | 1 |  | 01 NO.
58 | BWP-101A | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | BORE WELL PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L |  |  |  | 1 |  | 01 NO. | CAP.-20 M3/Hr | 20
59 | BWP-101B | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | BORE WELL PUMP | WORKING | STAND BY | 3-ph, 415 V AC | D O L |  |  |  |  | 1 | 01 NO. | CAP.-20 M3/Hr | 20
60 | P-101A | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | RAW WATER TR. PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 2.2 | 3 | 2.2 | 1 |  | 01 NO. | CAP.-12 M3/Hr | 12 | 20 | 1000 | 0.5 | 1.3262 | 1.6578 | 2.2
61 | P-101B | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | RAW WATER TR. PUMP | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 2.2 | 3 |  |  |  | 01 NO. | CAP.-12 M3/Hr | 12 | 20 | 1000 | 0.5 | 1.3262 | 1.6578 | 2.2
64 | P-118A | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | DW & SW FEED PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 3 | 4 | 0.15 | 1 |  | 01 NO. | CAP.-12 M3/Hr | 12 | 30 | 1000 | 0.5 | 1.9893 | 2.4867 | 3
65 | P-118B | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | DW & SW FEED PUMP | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 3 | 4 |  |  | 1 | 01 NO. | CAP.-12 M3/Hr | 12 | 30 | 1000 | 0.5 | 1.9893 | 2.4867 | 3
66 | P-120A | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | RO WATER TRANSFER PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 3 | 4 | 3 | 1 |  | 01 NO. | CAP.-12 M3/Hr | 12 | 30 | 1000 | 0.5 | 1.9893 | 2.4867 | 3
67 | P-120B | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | RO WATER TRANSFER PUMP | WORKING | STAND BY | 3-ph, 415 V AC | D O L | 3 | 4 |  |  | 1 | 01 NO. | CAP.-12 M3/Hr | 12 | 30 | 1000 | 0.5 | 1.9893 | 2.4867 | 3
70 | DMFBP-101 | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | DUEL MEDIA FILTER BACK WASH PUMP | WORKING | CONTINUOUS | 3-ph, 415 V AC | D O L | 5.5 |  |  | 1 |  | 01 NO. | CAP.-12 M3/Hr | 12
71 | CU-101 | BTIT/5TPD/PFD-002 (SHT-1 TO 3) | CHLORINATION UNIT | WORKING | CONTINUOUS | 1-ph, 230 V AC | D O L |  |  |  | 1 |  | 01 NO. | CAP.-XX
72 |  | BTIT/5TPD/PFD-002 (SHT-3 TO 3) | COMPRESSED AIR COMPRESSURE | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 3.7 |  |  | 1 |  | 01 NO.
73 |  | BTIT/5TPD/PFD-002 (SHT-3 TO 3) | INSTRUMENT AIR COMPRESSURE | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 2.2 |  |  | 1 |  | 01 NO.
74 |  |  | FURNACE | WORKING | CONTINUOUS | 3-ph, 415 V AC | SUPPLY | 15 |  |  | 1 |  | 01 NO.

## Sheet1 (hidden)
List of Inquiry sent to vendors for 5TPD Silica Plant
dated: 19.12.2019.
SL NO. | DOCUMENT NAME | VENDOR NAME | VENDOR CONTACT | REMARKS
1 | RFQ 01_Pumps Coversheet
2 | RFQ-01-Pumps-Annexure-A | Debson Pumps Private Limited, 14, Gujrat Mansion, Ground Floor, Bentick Street, Ganesh Chandra Ave, Chowringhee North, Bow Barracks, Kolkata, West Bengal 700001 | Mr. Joydeep dutta, 090073 93846, E-mail: kanak.mujumdar@kbl.co.in
3 | RFQ 02_Filter Press Coversheet
4 | RFQ-02-Filter press-Annexure-A | SACHIN INDUSTRIES LTD AHMEDABAD-INDIA. TEL: +91-79-25832204/05/9099082714 M: +91-9427613146 | Mr. Parth Patel, E-mail: parth@sachininternational.com
5 | RFQ 04_Conveyors Coversheet
6 | RFQ-04_ Conveyors-Annexure-A | EMTICI ENGINEERING LTD. Anand - Sojitra Road, Vallabh Vidyanagar-388 120 Gujarat (India) | Mr. R Haridoss. +91 944320 11536. E-mail: rharidoss@emtici.co.in
|  | Mecgale Pneumatics Pvt. Ltd. N-65, MIDC, Hingna Road, Nagpur 440016 INDIA | Kind attention Mr. Pankaj Saha. +91 92305 77974, E-mail: pankaj.saha@mecgale.com ; prasun.acharyya@mecgale.com
7 | RFQ 05_Driers Coversheet
8 | RFQ-05_Drier-Annexure-A | MOJJ ENGINEERING SYSTEMS LTD., 58 & 59A, 2nd Floor , Rudraksha Complex II , Plot No. 1606 , Phase 3,, Opposite Annapurna restaurant, GIDC VATVA, Ahmedabad - 382445 | Mr. Naresh Khatwani (mobile: +91 - 9662538670) E-mail: naresh.khatwani@mojjpune.com
|  | Drying Systems India Pvt Ltd | Mr. K. C. Pattanayak (09819773063), E-mail: drying01@yahoo.com
9 | RFQ 09_Steam Boiler Coversheet
10 | RFQ-09_Steam Boiler-Annexure-A | Multitech Boilers Private Limited 12A Kalibari Lane Jadavpur Kolkata Pin - 700032 Tel: + 91 33 2483 8315 Fax: + 91 33 2414 8252 | Mr. Samaresh Biswas, E-mail: mltechboilers@gmail.com
11 | RFQ-10_Tanks Coversheet
12 | RFQ-10_Tanks-Annexure-A | GMM Pfaudler | Arup Mitra.Ph: 6352490986, Email : arup.mitra@gmmpfaudler.com
|  | Fabricator | Kind attention Mr. Nayan Sengupta (+91 9831746680), E-mail: nayan.sengupta@gmail.com
|  | Fero Mecha Equipment Process Pvt. Ltd. 7/1A Grant Lane, Ganpati Chambers 3rd Floor, Kolkata:, 700012. | Mr. Sukhen Pal. (+91 9831746680), E-mail: feromecha@gmail.com
13 | RFQ-11-Agitator Coversheet
14 | RFQ-11-Agitator-Annexure-A | GMM Pfaudler | Arup Mitra.Ph: 6352490986, Email : arup.mitra@gmmpfaudler.com
|  | Agitators & Mixing Solutions, 31, Nonadanga Road, Sheoraphuly, Hooghly, W. Bengal- 712223. | Rakesh Dey, E-mail: aginmsol@yahoo.co.in

## Sheet2 (hidden)
flow | head | density | eficiency | power | margin | selected motor
m3/hr | mwc | kg/m3 | in decimal | bkw | in decimal | kw
50 | 105 | 1000 | 0.8 | 18.1319 | 22.6649

## SUPERSEEDED (hidden)
EQUIPMENT LIST FOR 20 TPD SILICA PLANT
| TAG NO. | EQUIPMENT NAME | CAPACITY(EXISTING) | CAPACITY(NEW) | QTY | MOC | W | L | H | VOL.
1 | AS-101 | WET ASH STORAGE AREA | CAP.-175 M3 | CAP.-175 M3 | 01 NO. |  | 10 | 9 | 2 | 180
2 | SCN-101 | WET ASH CONVEYOR | CAP.-2600 KG/HR. | CAP.-2500 KG/HR. | 01 NO.
3 | AD-101 | ASH DRIER-1 | CAP.-1700 KG/HR. | CAP.-655 KG/HR. | 01 NO.
4 | SCN-102 | DRY ASH CONVEYOR | CAP.-1700 KG/HR. | CAP.-1700 KG/HR. | 01 NO.
5 | DH-102 | DRY ASH STORAGE | CAP.- 224 M3 | CAP.- 219 M3 | 01 NO. |  | 8 | 14 | 2 | 224
6 | BCN-103 | ASH FEED UNIT | CAP.-6700Kg/Hr | CAP.-6600 Kg/Hr | 01 NO.
7 | AMV-101 | ASH MIXING VESSEL | CAP.- 90 M3 | NOT REQUIRE
8 | P-102A/B | ASH SLURRY TRANSFER PUMP | CAP.-150 M3/Hr | NOT REQUIRE
9 | DG-01/DG-02 | DIGESTER | CAP.-45 M3, dT-90-170°C | CAP.-45 M3 | 02 NOS.
10 | T-102 | DIGESTED SLURRY FLASH TANK | CAP.-90 M3 | NOT REQUIRE
11 | P-103A/B | FEED PUMP FOR ASH FILTER PRESS | CAP.- 150 M3/Hr | CAP.- 73 M3/Hr | 02 NOS.
12 | BCN-104A/B | UNDIGESTED ASH CONVEYOR | CAP.- 5900 KG/HR | CAP.- 5900 KG/HR | 02 NOS.
13 | F-101 | ASH FILTER PRESS | CAP.- 150 M3/Hr. | CAP.- 73 M3/Hr. | 01 NO.
14 | T-105 | SODIUM SILICATE TANK | CAP.- 80 M3 | CAP.- 80 M3 | 01 NO.
15 | MIX-101 | STATIC MIXER | CAP.-150 M3/Hr. | CAP.-73 M3/Hr. | 01 NO.
16 | PR-101A/B | PRECIPITATOR | CAP.-40 M3, | CAP.-40 M3, | 02 NOS. | SS-304
17 | EP-101A/B/C | CO2 EJECTOR PUMP | CAP.- 180M3/Hr. | CAP.- 150 M3/Hr. 5 KG/CM2 | 03 NOS.
18 | CG-101 | CO2 BULET AND VAPOURISER | CAP.- 3600 KG/Hr, | CAP.- 1036 (MIN), 4141(MAX) KG/Hr, | 01 NO.
19 | P-107A/B | SILICA SLURRY PUMP-1 | CAP.- 150 M3/Hr, | CAP.- 72 M3/Hr, | 02 NOS. | SS-304
20 | F-102A/B | SILICA FILTER PRESS-1 | CAP.- 75 M3/Hr, | CAP.- 36 M3/Hr, | 02 NOS.
21 | V-101 | SILICA CAKE LIQUIFICATION VESSEL-1 | CAP.- 42 M3 | CAP.- 42 M3 | 01 NO. | SS-304
22 | P-108A/B | SILICA SLURRY PUMP-2 | CAP.-150 M3/Hr | CAP.-70 M3/Hr | 02 NOS. | SS-304
23 | F-103A/B | SILICA FILTER PRESS-2 | CAP.-75 M3/HR | CAP.-35 M3/HR | 02 NOS.
24 | V-102 | SILICA CAKE LIQUIFICATION VESSEL-2 | CAP.- 75 M3 | CAP.- 73 M3 | 01 NO. | SS-304
25 | P-110A/B | SILICA SLURRY PUMP-3 | CAP.-150 M3/Hr | CAP.-70 M3/Hr | 02 NOS. | SS-304
26 | F-104A/B | SILICA FILTER PRESS-3 | CAP.-75 M3/Hr. | CAP.-36 M3/Hr. | 02 NOS.
27 | V-103A/B | SILICA CAKE LIQUIFICATION VESSEL-3 CUM NEUTRALISATION VESSEL | CAP.- 42 M3 | CAP.- 36 M3 | 02 NOS. | SS-304
28 | P-112A/B | SILICA SLURRY PUMP-4 | CAP.-150 M3/Hr | CAP.-60 M3/Hr | 02 NOS. | SS-304
29 | D-101 | SILICA SPRAY DRIER UNIT | CAP.-8500 KG/Hr | CAP.-8500 KG/Hr | 01 NO. | SS-304
30 | BCN-105 | PRODUCT SILICA CONVY. | CAP.-8500 KG/Hr | NOT REQUIRE |  | SS-304
31 | T-107 | SODIUM CARBONATE TANK | CAP.- 80 M3 | CAP.- 80 M3 | 01 NO.
32 | RE-101A/B | REGENERATOR UNIT | CAP.-43 M3 | CAP.-43 M3 | 02 NOS.
33 | SI-101 | Ca(OH)2 STORAGE | CAP.-205 M3 | CAP.-205 M3 | 01 NO.
34 | BCN-112 | Ca(OH)2 CONVEYOR-1 | CAP.-3300 KG/HR. | CAP.-1600 KG/HR. | 01 NO.
35 | BCN-113 | Ca(OH)2 CONVEYOR-2 | CAP.-3300 KG/HR. | CAP.-1600 KG/HR. | 01 NO.
36 | P-115A/B | CaCO3 SLURRY PUMP-1 | CAP.- 150 M3/Hr. | CAP.- 76 M3/Hr. | 02 NOS.
37 | F-105 | CaCO3 FILTER PRESS-1 | CAP.-150 M3/Hr. | CAP.-76 M3/Hr. | 01 NO.
38 | V-105 | CaCO3 LIQUIFICATION VESSEL -1 | CAP.-6 M3 | CAP.-9 M3 | 01 NO.
39 | P-116A/B | CaCO3 SLURRY PUMP-2 | CAP.-12 M3/Hr. | CAP.-15 M3/Hr. | 02 NOS.
40 | F-106 | CaCO3 FILTER PRESS-2 | CAP.-12 M3/Hr. | CAP.-15 M3/Hr. | 01 NO.
41 | BCN-107 | CaCO3 SPIN DRIER FEED CONVY. | CAP.-925 KG/Hr | NOT REQUIRE
42 | D-102 | CaCO3 SPRAY DRIER | CAP.-600 KG/Hr. | CAP.-450 KG/Hr. | 01 NO.
43 | BCN-108 | PRODUCT CaCO3 CONVY. | CAP.-925 KG/Hr | CAP.-925 KG/Hr | 01 NO.
44 | T-101 | CAUSTIC LYE STORAGE TANK | CAP.- 25 M3 | CAP.- 25 M3 | 01 NO.
45 | P-101A/B | CAUSTIC LYE TRANSFER PUMP | CAP.- 20 M3/Hr | CAP.- 20 M3/Hr | 02 NOS.
46 | T-103 | CAUSTIC DILUTION TANK | CAP.- 75 M3 | CAP.- 73 M3 | 01 NO.
47 | P-105A/B | DIL. CAUSTIC LYE TR. PUMP | CAP.- 75 M3/Hr | CAP.- 73 M3/Hr | 02 NOS.
48 | T-106 | FEED WATER TANK | CAP.- XX M3 | CAP.- XX M3 | 01 NO. | 20
49 | BLR-101 | STEAM BOILER | CAP.-7 TPH | CAP.-7.0 TPH | 01 NO.
50 | PRS-101 | PRESSURE REDUCING STATION | CAP.-6 TPH/hr | NOT REQUIRE
51 | TRS-101A/B | TRAP STATION | CAP.-2.5 BAR(A) | CAP.-1.5 BAR(A) | 02 NOS.
52 | T-110 | FILTERED WATER TANK | CAP.- 30 M3 | CAP.- 22 M3 | 01 NO.
53 | T-108 | CONC. H2SO4 TANK | CAP.-5 M3 | CAP.-3 M3 | 01 NO.
54 | P-113A/B | CONC. H2SO4 TR. PUMP | CAP.-2 M3/Hr | CAP.-2 M3/Hr | 02 NOS.
55 | T-109 | DIL. H2SO4 TANK | CAP.-5 M3 | CAP.-3 M3 | 01 NO.
56 | P-114A/B | DIL. H2SO4 TR. PUMP | CAP.-2 M3/Hr | CAP.-2 M3/Hr | 02 NOS.
57 | AG-01 | AGITATOR FOR DIGESTOR |  |  | 01 NO.
58 | AG-10 | AGITATOR FOR CAUSTIC DILUTION TANK |  |  | 01 NO.
59 | AG-02 | AGITATOR FOR DIGESTOR |  |  | 01 NO.
60 | AG-03 | AGITATOR FOR DIGESTED SLURRY FLASH TANK |  | NOT REQUIRE
61 | AG-04A/B | AGITATOR FOR PRECIPITATOR |  |  | 02 NOS.
62 | AG-06 | AGITATOR FOR SILICA CAKE LIQUIFICATION VESSEL-1 |  |  | 01 NO.
63 | AG-07 | AGITATOR FOR SILICA CAKE LIQUIFICATION VESSEL-2 |  |  | 01 NO.
64 | AG-08A/B | AGITATOR FOR SILICA CAKE LIQUIFICATION VESSEL-3 |  |  | 02 NOS.
65 | AG-11 | AGITATOR FOR DIL. H2SO4 TANK |  |  | 01 NO.
66 | AG-05A/B | AGITATOR FOR REGENERATORS |  |  | 02 NOS.
67 | AG-09 | AGITATOR FOR CaCO3 LIQUIFICATION VESSEL-2 |  |  | 01 NO.
68 | BWP-101A/B/C | BORE WELL PUMP | CAP.-25 M3/Hr. | CAP.-30 M3/Hr. | 03 NOS.
69 | T-104 | RAW WATER STORAGE TANK | CAP.- 500 M3 | CAP.- 300 M3 | 01 NO. |  | 15 | 10 | 3.4 | 510
70 | P-121 A/B | FILTER FEED PUMP | CAP.-61 M3/Hr. | CAP.-48 M3/Hr. | 02 NOS.
71 | OC-101 | OXIDISATION CHAMBER | CAP.-61 M3/Hr. | CAP.-48/ M3/Hr. | 01 NO.
72 | IRF-101 | IRON REMOVAL FILTER | CAP.-61 M3/Hr. | CAP.-48/ M3/Hr. | 01 NO.
73 | T-114A/B/C/D | DRINKING WATER TANK | CAP.-1.0 M3 | CAP.-1.0 M3 | 04 NOS.
74 | P-118A/B | RO FEED PUMP | CAP.-61 M3/Hr. | CAP.-48/ M3/Hr. | 02 NOS.
75 | T-111A/B/C | SW & DW TANK | CAP.-2 M3/Hr. | CAP.-2 M3/Hr. | 03 NOS.
76 | P-120A/B | RO WATER SUPPLY PUMP | CAP.- 30 M3/HR. | CAP.- 24 M3/HR. | 02 NOS.
77 | ROP-101 | RO PLANT | CAP.- 38 M3/HR. | CAP.- 32 M3/HR. | 01 NO.
78 | T-112 | RO DISTRIBUTION TANK | CAP.-60 M3 | CAP.- 50 M3 | 01 NO.
79 | CU-101 | CHLORINATION UNIT | CAP.-xx | CAP.-xx | 01 NO.
80 | T-113A/B | RO WATER STORAGE TANK | CAP.- 150 M3 | CAP.- 130 M3 | 02 NOS.
81 | P-109A/B | SODIUM SILICATE TR. PUMP | CAP.- 150 M3/Hr | CAP.- 73 M3/Hr | 02 NOS.
82 | P-111A/B | SODIUM CARBONTE FEED PUMP | CAP.-150 M3/Hr | CAP.-72 M3/Hr | 02 NOS.
83 | ACMP-1.00 | COMPRESSOR-1 |  | CAP-2.5 NM3/MIN. | 01 NO.
84 | ACMP-2.00 | COMPRESSOR-2 |  | CAP-2.5 NM3/MIN. | 01 NO.
85 | ACMP-3.00 | COMPRESSOR-3 |  | CAP-2.5 NM3/MIN. | 01 NO.
86 | RDR-1.00 | DESICCANT DRIER-1 |  | CAP-2.5 NM3/MIN. | 01 NO.
87 | ARCV-1.00 | AIR RECEIVER-1.00 |  | CAP-2.5 NM3/MIN. | 01 NO.
88 | ARCV-2.00 | AIR RECEIVER-2.00 |  | CAP-2.5 NM3/MIN. | 01 NO.
89 | AQM-1.00 | ACCUMULATOR-1 |  | CAP-1.0 M3 | 1 NO.
90 | AQM-2.00 | ACCUMULATOR-2 |  | CAP-1.0 M3 | 1 NO.
91 | FFC-101 | FEED CONVEYOR TO FURNACE |  | CAP. - XXXXX | 01 NO.
92 | FUR-101 | BIOMASS FURNACE |  | RATING -8698911 KCAL/HR | 01 NO.
93 | HAG -101 | HOT AIR GENERATOR |  | RATING - 7302070 KCAL/HR | 01 NO.
94 | MDC -101 | MECHANICAL DUST COLLECTOR |  | CAP. - XXXXX | 01 NO.
95 | CAF -101 | COMBUSTION AIR FAN |  | CAP. - XXXXX | 01 NO.
96 | CHMN -101 | CHIMNEY |  |  | 01 NO.
97 | PAF - 101 | PROCESS AIR FAN |  | CAP. - XXXXX | 01 NO.
98
99
100
NB: | RED COLOURED FONT | = | EXISTING
| GREEN COLOURED | = | AS PER NEW CALCULATION

## Cover Sheet
Owner: HINDALCO INDUSTRIES LIMITED Ahura Centre, 1st Floor, B Wing, Mahakali Caves Road, Andheri (East), Mumbai - 400 093, India
EPCM Contractor: W. L. GORE & ASSOCIATES (Pacific) Pte, Ltd. India Branch 703, A-Wing, 215 Atrium, Andheri Kurla Road, Mumbai 400059, India
Nominated Subcontractor - Engineering, Quality Control, Supervision: SMARTLuth Solution and Service Pvt. Ltd. Unit No: 503, 5th Floor, ECO Centre,. EM-4 Sector-V, Salt Lake City, Kolkata - 700091, India
Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant
Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System
FGD - Electrical Load List
1 | 2022-03-01 | REVISED AS MARKED |  | S.Das |  | S.Chakraborty |  | M.Deb
0 | 2022-02-23 | First Issue |  | S.Das |  | S.Chakraborty |  | M.Deb
Rev. | Date | Description of revision |  | Prepared |  | Checked |  | Approved
Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant |  |  |  | Drg. / Doc. No. : S21001- EN01 - 05HSD - 331002
Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System |  |  |  | Gore Doc. No.: RPDU5.EM.000 |  |  | page 1 |  | of | 2
FGD - Electrical Load List |  |  |  | GORE Job : RPDU5 |  |  | Rev. : | 1
|  |  |  | File: | FGD - Electrical Load List -R1_dated 01.03.2022
This document is a property of W.L. GORE & ASSOCIATES (Pacific) Pte, Ltd. and it may contain trade secrets or privileged, undisclosed or otherwise confidential information. If you have received this document in error, you are hereby notified that any review, copying or distribution of it is strictly prohibited.

## FGD Load List
FGD - Electrical Load List
10 |  | Hindalco Doc No: S21001- EN01 - 05HSD - 331002 |  |  | Rev-1 | [13 empty] | Date: 01.03.2022
WL Gore Doc No: RPDU5.EM.000
| Sl.no | Item name of drive units | Tag no's | P&ID Ref. No. | Working | Stand by | Duty |  |  | Feeder Type | Starter Type | VOLTAGE |  | Power consumption | Motor Power rating |  | SOV Power rating | Feeder Rating | Remarks | DUTY | VOLTAGE | CONNECTION | flow | head | density | efficiency | power | margin | selected motor
[7 empty] | CONTINUOUS | INTERMITTENT | STAND BY |  |  | 3-Phase ,50 HZ, AC | Single Phase , 50 HZ, AC | BKW | KW | HP | KW | [5 empty] | m3/hr | mmwc | kg/m3 | in decimal | bkw | in decimal | kw
| 1 | MIST-ELIMINATOR/OHT FGTR MAKE-UP/ ASH FILTER- FRESH WATER PUMP-A | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS |  |  | DRIVE | D O L | 415 V |  | 13.2622 | 18.5 | 25 | [6 empty] | 40 | 60 | 1000 | 0.5 | 13.2622 | 16.5778 | 18.5
| 2 | MIST-ELIMINATOR/OHT FGTR MAKE-UP/ ASH FILTER- FRESH WATER PUMP-B | LATER | S21001-XFXX-05HSD-227XX |  | 1 |  |  | STAND BY | DRIVE | D O L | 415 V |  |  | 18.5 | 25 | [6 empty] | 40 | 60 | 1000 | 0.5 | 13.2622 | 16.5778 | 18.5
| 3 | PROCESS WATER PUMP -A | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS |  |  | DRIVE | D O L | 415 V |  | 29.84 | 40 | 54 |  |  | R1 |  |  |  | 36 | 190 | 1000 | 0.5 | 37.7973 | 47.2467 | 50
| 4 | PROCESS WATER PUMP -B | LATER | S21001-XFXX-05HSD-227XX |  | 1 |  |  | STAND BY | DRIVE | D O L | 415 V |  |  | 40 | 54 |  |  | R1 |  |  |  | 36 | 190 | 1000 | 0.5 | 37.7973 | 47.2467 | 50
| 5 | FGTR MODULE WASH PUMP-A | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS |  |  | DRIVE | D O L | 415 V |  | 35.92 | 50 | 67 |  |  | R1 |  |  |  | 53 | 65 | 1000 | 0.5 | 19.0368 | 23.796 | 25
| 6 | FGTR MODULE WASH PUMP-B | LATER | S21001-XFXX-05HSD-227XX |  | 1 |  |  | STAND BY | DRIVE | D O L | 415 V |  |  | 50 | 67 |  |  | R1 |  |  |  | 53 | 65 | 1000 | 0.5 | 19.0368 | 23.796 | 25
| 7 | PUMP TO CLIENT SERVICES-A | LATER | S21001-XFXX-05HSD-227XX | 1 |  |  | INTERMITTENT |  | DRIVE | D O L | 415 V |  | 2.4867 | 3.7 | 5 | [6 empty] | 15 | 30 | 1000 | 0.5 | 2.4867 | 3.1083 | 3.7
| 8 | PUMP TO CLIENT SERVICES-B | LATER | S21001-XFXX-05HSD-227XX |  | 1 |  |  | STAND BY | DRIVE | D O L | 415 V |  |  | 3.7 | 5 | [6 empty] | 15 | 30 | 1000 | 0.5 | 2.4867 | 3.1083 | 3.7
| 9 | FGTR EFFLUENT TRANSFER PUMP-A | LATER | S21001-XFXX-05HSD-227XX | 1 |  |  | INTERMITTENT |  | DRIVE | D O L | 415 V |  | 5.3049 | 7.5 | 10 |  |  | R1 |  |  |  | 12 | 80 | 1000 | 0.5 | 5.3049 | 6.6311 | 7.5
| 10 | FGTR EFFLUENT TRANSFER PUMP-B | LATER | S21001-XFXX-05HSD-227XX |  | 1 |  |  | STAND BY | DRIVE | D O L | 415 V |  |  | 7.5 | 10 |  |  | R1 |  |  |  | 12 | 80 | 1000 | 0.5 | 5.3049 | 6.6311 | 7.5
| 11 | SAC INLET PUMP-A | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS |  |  | DRIVE | D O L | 415 V |  | 1.9893 | 3.7 | 5 | [6 empty] | 12 | 30 | 1000 | 0.5 | 1.9893 | 2.4867 | 3.7
| 12 | SAC INLET PUMP-B | LATER | S21001-XFXX-05HSD-227XX |  | 1 |  |  | STAND BY | DRIVE | D O L | 415 V |  |  | 3.7 | 5 | [6 empty] | 12 | 30 | 1000 | 0.5 | 1.9893 | 2.4867 | 3.7
| 13 | SAC RECOVERED WATER -A | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS |  |  | DRIVE | D O L | 415 V |  | 2.6524 | 3.7 | 5 | [6 empty] | 12 | 40 | 1000 | 0.5 | 2.6524 | 3.3156 | 3.7
| 14 | SAC RECOVERED WATER -B | LATER | S21001-XFXX-05HSD-227XX |  | 1 |  |  | STAND BY | DRIVE | D O L | 415 V |  |  | 3.7 | 5 | [6 empty] | 12 | 40 | 1000 | 0.5 | 2.6524 | 3.3156 | 3.7
| 15 | SAC START-UP RECIRCULATION PUMP -A | LATER | S21001-XFXX-05HSD-227XX | 1 |  |  | INTERMITTENT |  | DRIVE | D O L | 415 V |  | 0.082889 | 0.25 | 1 | [6 empty] | 1 | 15 | 1000 | 0.5 | 0.082889 | 0.10361 | 0.25
| 16 | SAC START-UP RECIRCULATION PUMP -B | LATER | S21001-XFXX-05HSD-227XX |  | 1 |  |  | STAND BY | DRIVE | D O L | 415 V |  |  | 0.25 | 1 | [6 empty] | 1 | 15 | 1000 | 0.5 | 0.082889 | 0.10361 | 0.25
| 17 | CONCENTRATED ACID LOADING PUMP -A | LATER | S21001-XFXX-05HSD-227XX | 1 |  |  | INTERMITTENT |  | DRIVE | D O L | 415 V |  | 2.2104 | 3.7 | 5 | [6 empty] | 20 | 20 | 1000 | 0.5 | 2.2104 | 2.763 | 3.7
| 18 | CONCENTRATED ACID LOADING PUMP -B | LATER | S21001-XFXX-05HSD-227XX |  | 1 |  |  | STAND BY | DRIVE | D O L | 415 V |  |  | 3.7 | 5 | [6 empty] | 20 | 20 | 1000 | 0.5 | 2.2104 | 2.763 | 3.7
| 19 | BOOSTER FAN | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS |  |  | DRIVE | VFD | 690 V |  | 560 | 865 | 1154
| 20 | SAC SYSTEM | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS |  |  | SUPPLY |  | 415 V | [5 empty] | 400 | TENTATIVE, FEEDER RATING, R1
| 21 | MAIN LIGHT DISTRIBUTION PANEL | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS |  |  | SUPPLY |  | 415 V | [5 empty] | 100 | R1
| 22 | AC DISTRIBUTION BOARD | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS |  |  | SUPPLY |  | 415 V | [5 empty] | 100 | R1
| 23 | FIRE ALARM SYSTEM | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS |  |  | SUPPLY |  |  | 230 V |  |  |  |  | 32 | R1
| 24 | DOSING PUMP-A | LATER | S21001-XFXX-05HSD-227XX | 1 |  |  | INTERMITTENT |  | SUPPLY | D O L |  | 230 V |  | 0.37 | 0.5
| 25 | DOSING PUMP-B | LATER | S21001-XFXX-05HSD-227XX |  | 1 |  |  | STAND BY | SUPPLY | D O L |  | 230 V |  | 0.37 | 0.5
| 26 | AGITATOR OF DOSING TANK | LATER | S21001-XFXX-05HSD-227XX | 1 |  |  | INTERMITTENT |  |  |  |  | 230 V |  | 0.22 | 0.3
| 27 | MOTORISED VALVES AS PER P&ID | LATER | S21001-XFXX-05HSD-227XX | 38 |  |  | INTERMITENT |  | DRIVE | R D O L |  | 230 V | 20.9 | 0.55 | 0.8 |  |  | TOTAL POWER
| 28 | PILOT SOLENOID FOR PNEUMATIC ACTUAOR OF DAMPERS ON ID FAN TO CHIMENY | LATER | S21001-XFXX-05HSD-227XX | 2 |  |  | INTERMITENT |  | SUPPLY | ON-OFF |  | 230 V |  |  |  |  | 0.12 | TOTAL BASED ON POWER REQUIREMENT OF PILOT SOLENOID AS 0.06 KW
| 29 | PILOT SOLENOID FOR PNEUMATIC ACTUAOR OF DAMPERS ON TAP OFF LINE FROM ID FANS TO BOOSTER FAN | LATER | S21001-XFXX-05HSD-227XX | 2 |  |  | INTERMITENT |  | SUPPLY | ON-OFF |  | 230 V |  |  |  |  | 0.12
| 30 | PILOT SOLENOID FOR PNEUMATIC ACTUAOR OF DAMPERS AT BOOSTER FAN SUCTION | LATER | S21001-XFXX-05HSD-227XX | 2 |  |  | INTERMITENT |  | SUPPLY | ON-OFF |  | 230 V |  |  |  |  | 0.12
| 31 | PNEUMATIC ACTUATED VALVES | LATER | S21001-XFXX-05HSD-227XX | 142 |  |  | INTERMITENT |  |  | ON-OFF |  | 230 V |  |  |  |  | 8.52 | TOTAL POWER
| 32 | PLC PANEL | LATER | S21001-XFXX-05HSD-227XX | 1 |  | CONTINUOUS | [5 empty] | 230 V |  |  |  |  | 5 | TENTATIVE, FEEDER
|  | TOTAL ABSORBED POWER except SAC plant | [10 empty] | TENTATIVE | 674.6488
|  | TOTAL ABSORBED POWER except SAC plant on continuous basis | [10 empty] | TENTATIVE | 643.664