|  |  | Owner: HINDALCO INDUSTRIES LIMITED Ahura Centre, 1st Floor, B Wing, Mahakali Caves Road, Andheri (East), Mumbai - 400 093, India |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | EPCM Contractor: W. L. GORE & ASSOCIATES (Pacific) Pte, Ltd. India Branch 703, A-Wing, 215 Atrium, Andheri Kurla Road, Mumbai 400059, India |  |  |  |  |  |
|  |  | Nominated Subcontractor - Engineering, Quality Control, Supervision: SMARTLuth Solution and Service Pvt. Ltd. Unit No: 503, 5th Floor, ECO Centre,. EM-4 Sector-V, Salt Lake City, Kolkata - 700091, India |  |  |  |  |  |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System FGD & SAC – Civil DBR - Design Basis Report ISSUED FOR; APPROVAL; INFORMATION; MANUFACTURING; CONSTRUCTION; AS-BUILT. |
| 01 | 17/03/2022 | Revised as per B & V comments | I. Bose | S. Chakraborty |  |  | KKR |
| 00 | 10/02/2022 | First Issue | I. Bose | S. Chakraborty |  |  | KKR |
| Rev. | Date | Description of revision | Prepared | Checked |  |  | Approved |
| Hindalco Renusagar U5 1 x 80 MW PF Captive Power Plant |  |  | Drg. / Doc. No.: S21001-EN01-05CPP-551008 |  |  |  |  |
| Flue Gas Desulfurization Project (FGD) with GORETM SO2 Control System |  |  | Gore Doc. No.: RPDU5.PG.503 |  |  | page 1 of 19 |  |
| FGD & SAC – Civil DBR - Design Basis Report |  |  | GORE Job No.: RPDU5 |  |  | Rev. : 01 |  |
|  |  |  | File: DBR For Civil R1 |  |  |  |  |
| This document is a property of W.L. GORE & ASSOCIATES (Pacific) Pte, Ltd. and it may contain trade secrets or privileged, undisclosed or otherwise confidential information. If you have received this document in error, you are hereby notified that any review, copying or distribution of it is strictly prohibited. |  |  |  |  |  |  |  |

Contents							Page No.

- General									3

  - Scope of Work							4

  - Units of measurement					4

  - Applicable Codes						4

  - Site conditions							8

- General Design Considerations					8

2.1	 Design Loads							8

2.2	 Basic Load Cases						11

2.3 Load Combinations						11

2.4	 Reinforced Concrete Design				13

2.5 Steel Structure Design					17

1	GENERAL

1.01	This section of DBR covers the technical requirements for preparation of design, preparation

of GA drawing, design drawing of civil & structural works of the facilities included in the scope of FGD system.

1.02	Description of various items of work under this DBR are given hereinafter. The complete 	works under this DBR is referred to as “Civil & Structural Design Works”

1.03	The works to be performed under this DBR shall also include revisions & amendments 	thereto.

1.04	This DBR is intended for the general description of technical specification that should be adhered to at the minimum level.  In the event of absence of any relevant Indian standards, design should be carried out complying the requirements of relevant latest American/British standards/instructions of the Engineer-In-Charge/best prevailing practices but with complete satisfaction of owner. The list of IS codes to be followed is given elsewhere in this DBR.

1.05	Proprietary items like FGTR equipment (hot part), MCU equipment and their 	design/construction methodology are excluded from this DBR

1.1	Scope of work

Following items have been envisaged to be covered under the scope of work of this DBR

a.	Structural design of FGTR support (Cold part), platform & gallery of FGTR (cold 		part), stair tower on both sides of FGTR & chimney supported on FGTR

b.	RC foundation design of FGTR Support structure, PWT & FWT and other tanks, Ash Filter, Stair tower on both sides of FGTR

c.	Structural design of MCU support (Cold part), platform & gallery of MCU (cold part)

d.	RC foundation design of MCU Support structure

e.	RC foundation design of Booster Fan

f.	Structural design of Duct support structure

g.	RC foundation design of Duct Support Structure

h.	RC foundation of waste water tank, concentrated acid tank & recovered water tank

i.	RC foundation design of various pump-motor

j.	RC Foundation design of one multilevel structural building housing plant equipment and vessel. However, structure design is excluded.

k. 	Design of structure of RCC control room of acid plant.

1.2	Units of measurements

For all design documents and drawing, SI units will be considered

1.3	Applicable codes

All applicable standards, references, specification, codes of practices etc. shall preferably be 	the latest edition (unless noted otherwise or allowed by Engineer-In-Charge) including all 	applicable official amendments and revisions. A list of all these codes are detailed below.

IS:2720	Part – II, IV to VIII, XIV, XXI, XXIII, XXIV, XXVII to XXIX, XL)		IS:4701	Code of practice for earth work on canals.

IS:9758	Guide lines for dewatering during construction.

IS:10379	Code of practice for field control of moisture and compaction of soils for 				embankments & subgrade.

IS:280	Spec. For mild steel wire for general engineering purpose.

IS:456	Code of practice for plain and reinforced concrete.

IS:516	Method of test for strength of concrete.

IS:650	Specification of standard sand for testing of cement.

IS:1199	Methods of sampling and analysis of concrete.

IS:2502	Code of practice for bending and fixing of bars for concrete reinforcement.	IS:2505	General requirements for concrete vibrators, immersion type.

IS:2645	Specification for integral cement water proofing compounds.

IS:2750	Specification for steel scaffolding.

IS:2751	Code of practice for welding of mild steel column and deformed bars for RCC.	IS:3025	Method of sampling and test waste water.

IS:3370	Code of practice for concrete structures for the storage of liquids.

IS:3414	Code of practice for design and installation of joints in buildings.

IS:3558	Code of practice for use of immersion vibrators for consolidating concrete.

IS:4014	Code of practice for steel tubular scaffolding.

IS:4326	Code of practice for earthquake resistant design and construction of buildings.	IS:4990	Specification for plywood for concrete shuttering work.

IS;5525	Recommendation for detailing of reinforcement in RC work.

IS:5624	Specification for foundation bolts.

IS:6509	Code of practice for installation of joints in concrete pavements.

IS:9103	Specification for admixtures for concrete.

IS:9417-1989	Recommendation for welding cold worked steel bars for RCC.

IS:9417-2018   Welding of High Strength Steel Bars for Reinforced Concrete Construction 			        Recommendations

IS:10262	Recommended guidelines for concrete mix design

IS:13311	Method of non-destructive testing of concrete

SP:24		Explanatory handbook on IS:456-1978

SP:34		Handbook on concrete reinforcement and detailing

SP:16		Design aids for reinforced concrete to IS:456

IS:1905	Code of practice for structural safety of buildings-masonry walls

IS:2212	Code of practice for brickwork

IS:2250	Code of practice for preparation and use of masonry mortar

SP:20		Explanatory handbook on masonry code

IS:2016	Specification for plain washer

IS:814	Specification for covered electrodes for metal arc welding for weld steel		IS:3502	Specification for chequered plate

IS:6911	Specification for stainless steel plate, sheet & strip

IS:3757	Specification of high strength structural bolts

IS:6623	Specification for high strength structural nuts

IS:6649	High tensile friction grip washers

IS:800-1984	Code of Practice for use of structural steel in general building construction

IS:816 	Code of construction for use of structural steel in general building 					construction

IS:9595	Code of procedure of manual metal arc welding of mild steel

IS:7215	Tolerances for fabrication of steel structures

IS:12843	Tolerances for erection of structural steel

SP:6		Handbook of structural engineers

IS:1080	Code of practice for design and construction of simple spread foundations	IS:1904	Code of practice for design and construction of foundations in soils general 			           requirement simple spread foundations

IS:2950	Code of practice for design and construction raft foundation

IS:2974	Code of practice for design and construction of machine foundations

IS:6403	Code of practice for determination of allowable bearing pressure on shallow 				foundation

IS:8009	Code of practice for calculation of settlement of foundation subject to 					symmetrical vertical load

IS:12070	Code of practice for design and construction of shallow foundations on 				rocks

IS:875	Code of practice for design loads other than earthquake for buildings and 				structures

IS:1893	Criteria of earthquake resistant design of structures

IS:6533	Code of practice for design and construction of steel chimneys

R1

1.4  Site Condition

Location	The plant is located at Renusagar, Sonebhadra district, Uttar Pradesh,

45 km away from the Renukoot aluminium plant.

Latitude	24.18246

Longitude	82.79228

Mean Sea Level 		276.0M

Occupancy Category 	Industrial Building(IS:875-Part 2 Cl#2.2.4)

Wind Design Data	As detailed hereinafter under section 2.1 c.

Seismic Design Data	As detailed hereinafter under section 2.1 d.

2	GENERAL DESIGN CONSIDERATIONS

2.1	Design Loads

a.	Dead Load (DL)

Following unit weights will be considered for computation of dead loads

RCC	25	kN/m3

PCC	24	kN/m3

Structural Steel	   78.5 kN/m3

Stainless steel gr. 317LMN 	80 kN/m3

Liquid in FGTR	          11 kN/m3

PVC Pipe	                      13.8 kN/m3

Glass Coating	             16  kN/m3

FGTR module Dry wt	  0.4 kN /piece

FGTR module Wet wt	0.8 kN /piece

Dry Dust                                 10 kN/m3

R1

Soil                                          18  kN/m3

b.	Imposed Load(IL)

Following imposed load will be considered for computation

Stair tower/landing	                                   	 2.5	kN/m2

Gallery/platform for normal operation		  2.5	kN/m2

Gallery/platform for Module swapping/resting 7.5	kN/m2

Chimney platform	                                       	  2.5	kN/m2

Damper/Exp. Jt in duct platform	               	  2.5	kN/m2

Duct internal pressure upto booster fan            - 4.0 kN/m2

Thickness of dust in horizontal duct		  150	mm

c.	Wind Load

Basic Wind Speed	  39	m/s

K1	1.06

Terrain category	3

K3	1

K4	1

R1

K2	as per height

d.	Seismic Load

Zone	III

Importance factor	1.75

Method Seismic Coeff. Method

Soil Condition	Type – II (Medium)

Damping Factor	2.00%	    for steel structure

Damping Factor	5.00%	for concrete structure

e.	Temperature Load

Max. Temp.	45 deg C

Min Temp.	10 deg C

Operational temp.	53oC

For temp. Loading, the total temp variation shall be considered as 2/3rd of the average maximum annual variation in temperature. The average maximum annual variation in temp for this purpose shall be taken as the difference between the mean of the daily minimum ambient temp during the coldest month of the year and mean of daily maximum ambient temp during the hottest month of the year. The structures shall be designed to withstand stress due to 50% of the total temperature Variation.

Frictional load due to thermal expansion shall be suitably considered be providing bridge bearing as per relevant standard.

R1

f.	Earth Pressure

of soil	29o

Earth pressure for all underground structures shall be calculated using coeff. of active 		earth pressure. Passive earth pressure shall be used in design of shear keys for 			stability against sliding

2.2	Basic load cases

a.	Dead Load(DL)

b.	Imposed Load(IL)

c.	Dust

d.	Water/Liquid

e.	Seismic Load

f.	Wind Load

g.	Earth Pressure

2.3	Load Combination

For analysis & design following load combinations will be used with respective 			factors as per code

DL+IL

DL+IL+Dust

DL+Dust

DL+Water+IL

DL+Water+IL+Dust

DL+IL+Wind

DL+IL+Dust+Wind

DL+Dust+wind

DL+Water+IL+Wind

DL+Water+IL+Dust+wind

DL+Wind

DL+IL+Seismic

DL+IL+Dust+Seismic

DL+Dust+Seismic

DL+Water+IL+Seismic

DL+Water+IL+Dust+Seismic

R1

DL+Seismic

b. For strength design

1.5(DL+IL)

1.5(DL+IL+Dust)

1.5(DL+Dust)

1.5(DL+Water+IL)

1.5(DL+Water+IL+Dust)

1.2(DL+IL+Wind)

1.2(DL+IL+Dust+Wind)

1.2(DL+Dust+Wind)

1.2(DL+Water+IL+Wind)

1.2(DL+Water+IL+Dust+wind)

1.5(DL+Wind)

1.2(DL+IL+Seismic)

1.2(DL+IL+Dust+Seismic)

1.2(DL+Dust+Seismic)

1.2(DL+Water+IL+Seismic)

1.2(DL+Water+IL+Dust+Seismic)

1.5(DL+Seismic)

2.4	Reinforced Concrete Design

a.	Design Method

All RCC members to be designed as per Limit state method covered under IS:456.

b.	Utilized program

Software to be used for design will be STAAD Pro along with manual computation

c.	Material Specification: Cement

Fly ash based Portland pozzolana cement conforming to IS:1489(PART-1) shall preferably be used (unless required otherwise to counteract soil water chemical environment). However, Portland slab cement conforming IS:455 or ordinary Portland cement conforming to IS:269 or IS:8112 may also be used.

d.	Material Specification: Fine Aggregate

Sand shall be hard, durable, clean and free from adherent coatings of organic matter 		and clay balls or pellets. Sand, when used as fine aggregate in concrete shall conform 		to IS:383

e.	Material Specification: Coarse aggregate

Coarse aggregate for concrete shall be chemically inert, hard, strong, durable against weathering of limited porosity and free from deleterious materials. It shall be properly graded. It shall meet the requirement of IS:383

f.	Material Specification: Concrete

Minimum grade of concrete for various structures shall be M25 for underground/sub 		structural RCC work and all Super structural work. All RCC works to be done under this

DBR, unless specified shall be design mix concrete.

Minimum grade of PCC shall be M-7.5 and to be provided below all foundations with minimum 75 thickness.

Minimum grade of grout shall be M30

g.	Material Specification: Reinforcement Steel

Reinforcement steel shall conform to either Mild steel grade I of IS:432 part-1 and grade A of IS:2062 or High yield deformed bar of IS:1786(Fe 500) with minimum 14.5% elongation.

h.	Reinforcement Cover

Clear cover to main reinforcement for

Slab 20mm

Beam above ground 25mm

Beam below ground 30mm

Column and pedestal 40mm

R1

Foundation 50mm on all sides

i.	Minimum thickness

For slab 100mm

For beam width 300 mm

For beam depth 300mm

For column 300 mm

R1

For foundation – 250 mm

j.	Foundation design

For design of all underground structures, foundations, ground water level shall be 		assumed at FGL as considered in Geotech report calculations.

Footing of all major structure shall be so proportioned so as to minimise the 			differential settlement.

In case of foundations resting on soil/rock allowable bearing pressure may be 		increased upto 33% in case of seismic, wind load case.

The factor of safety against sliding of structures which resist lateral forces (such as 		retaining walls) shall be not less than 1.5 when dead load, imposed load and earth 		pressures are considered together with wind load or seismic forces. When dead load, 		imposed load and earth pressure only are considered, the factor of safety shall be not 		less than 1.75.

The factor of safety for shallow foundation against overturning shall be not less than 		1.5 when dead load, imposed load and earth pressures are considered together with 		wind load or seismic forces. When dead load, imposed load and earth pressures only 		are considered, the factor of safety shall be not less than 2.

The factor of safety for shallow foundation against uplift shall be not less than 			1.2 when dead load and wind load or seismic forces.

Permissible total settlement for foundations resting on soil or on rock shall be  40mm 		or 12 mm respectively.

Permissible differential settlement shall be 0.0033 times the distance between the columns for foundation either on soil or on rock.

Maximum crack width for liquid retaining structural elements is 0.2mm SBC of soil is 22

t/m2 at 3m depth.

Minimum Depth of Foundation shall be 2.0 M as recommended by soil investigation report

k.	Machine foundation design

All block foundations supporting rotating equipment resting on soil shall be 				designed using elastic half space theory. The mass of the RCC block shall not be less 		than three times the mass of the machine. Dynamic analysis shall be carried out to 			calculate natural frequencies in all the modes including coupled modes and to 			calculate vibration amplitudes. Frequency and amplitude criteria as laid down in the 		relevant codes shall be satisfied minimum reinforcement shall be governed by 			IS:2974 and IS:456

For the foundations supporting minor rotating equipment weighing less than ten 			kilonewton or if the mass of the rotating parts is less than one hundredth of the mass 		of the foundation, no dynamic analysis is necessary.

R1

2.5	Steel Structure Design

a.	Design Method

The design of steel structures shall be done by working stress method. Design shall 			be as per provision of IS:800-2007 and other relevant standards, wherever 				required.

b.	Material specification

Rolled sections and plates shall be of grade designation E250, Quality A and shall be 		semi-killed / killed conforming to IS:2062-2011. Plates shall be of grade 				designation E250, Quality BR, killed, tested for impact resistance conforming to 			IS;2062-2011. Plates beyond 20mm thickness and up to 40mm thickness shall be 			controlled rolling. Pipes for hand rail shall conform to IS:1161. Chequered plate shall 		conform to IS:3502 and shall be minimum 6mm thickness excluding projection. 			Steel for chequered plate shall conform to E250A grade semi killed of IS:2062.

Stainless steel to be used shall conform to SA:240 of ASTM (Spec for heat resisting 	chromium and chromium-nickel stainless steel plates, sheet and strip for pressure 		vessels)

c.	Weld

All structural components fabricated at shop will be having welded connections. For 		welding of structural parts IS:814, IS:816, IS:1024, IS:4353 and IS:9595 shall be 		          followed. Criteria for test of weld.  For FGTR, MCU & Chimney may have welded 		          connection at site too.

Visual examination: 100% of the welded joints for fillet welds and butt welds.

Ultrasonic method – 50% of all the butt welded joints

R1

d.	Connection bolt

All structural components fabricated at shop and erected at site will be having 			permanent bolted connections in general except for FGTR, MCU, Chimney & Duct. 		For bolt connection IS:4000, IS:3757, IS:6623 and IS:6649 shall be followed.

Bolts 	& nuts will be as per  minimum grade 8.8 to maximum grade of 12.9

e.	Minimum thickness/size

All stairs shall have a maximum riser height of 200mm and a minimum tread width of 230mm, Minimum clear width of stair shall be 1000 mm. Minimum head room under all floors, walkways and stairs shall be 2100

All ladders with or without cage shall be minimum 400 wide

Minimum thickness of grating shall be 25mm for outdoor and 32mm for indoor 			installation.

Handrail shall have top and middle rail at a height of 1000 mm and 500 mm and the vertical post spacing shall not be exceeding 1500   Hand rail members for top rail, post shall be 32NB(M), for mid rail shall be 25 NB(M) and for kick plates 100x4 flat shall be used.

f.	Permissible deflection

Maximum horizontal deflection for columns L/325 where L, effective length of the column shall be as per relevant IS code.

Vertical deflection for horizontal beam members span / 325.

For all beams directly supporting equipment, vertical deflection shall be limited to 			L/500. However FGTR casing support beam deflection shall be limited to L/1000.

For all grating/chequered plates vertical deflection shall be limited to L/250. However,

the maximum vertical deflection of grating/chequered plate shall be limited to 6m

g.	    Slenderness limits

Compression from DL and/or IL and/or Dust and/or Liquid/water  180

Tension from DL and/or Il and/or Dust and/or Liquid/water	300

Compression from DL and/or IL and/or Dust and/or Liquid/water and/or 				Wind/Seismic	250

Compression flange of beam	300

Tension from DL and/or IL and/or Dust and/or Liquid/water and/or Wind/Seismic			350

h.	Column base

For checking against uplift/tension case, 90% of Dead loads with no imposed load 			/dust load/water/Liquid will be considered. Following load combinations will be used 		for computing net uplift/tension in foundation bolts.

Wind load +/- 90% of dead load

Seismic load (considering dead load & liquid/water & imposed load within 				FGTR/MCU) +/- 90% of dead load & liquid/water & imposed load

R1

Seismic load (considering dead load) +/- 90% of dead load

i.	Storey Drift

The storey drift in any storey due to the minimum specified design lateral force, with 		partial load factor of 1.0, shall not exceed 0.004 times the storey height.