ELECTRIC  MOTORS

1.00.00	DESIGN CRITERIA

1.01.00	General

1.01.01	Motors shall be furnished in accordance with the accompanying driven equipment specification.

In case of any discrepancy, the driven equipment specification shall govern.

1.01.02	The motors will be installed in hot, humid and tropical atmosphere, highly polluted with coal dust.  Canopy to be provided to all outdoor or open to atmosphere, installed motors.

1.01.03	Unless otherwise noted, electrical equipment/system design shall be based on the service conditions and auxiliary power supply given in the  specification.

1.01.04	For motor installed outdoor and exposed to direct sun rays, the effect of solar heat shall be considered in the determination of the design ambient temperature.

2.00.00	STANDARDS

2.01.00   	All motors shall conform to the latest applicable IS, IEC and CBIP Standards/Publications except when otherwise stated herein or in the driven equipment specification.

2.02.00 	Major standards, which shall be followed, are listed below. Other applicable Indian Standards for any component part even if not covered in the listed standards shall also be followed :

IS-325

IS-12615

IEC-60034

3.00.00	TYPE & RATING

3.01.00	A.C. Motors

3.01.01	Motors shall be general purpose, constant speed, squirrel cage induction type, three/single phase.

3.01.02	All motors shall be rated for continuous duty.  They shall also be suitable for long period of inactivity.

3.01.03	The motor name-plate rating shall have at least 15% margin over the input power requirement of the driven equipment at rated duty point.

3.01.04	The motor characteristics shall match the requirements of the driven equipment so that adequate starting, accelerating, pull up, break down and full load torques are available for the intended service.

3.01.05	Motors located in hazardous area shall be flameproof type.

4.00.00	SPECIFIC REQUIREMENTS

4.01.00	Running Requirements

4.01.01	Motor shall run continuously at rated output over the entire range of voltage and frequency variations as given in the annexure.

4.01.02	The motor shall be capable of operating satisfactorily at full load for 5 minutes without injurious heating with 75% rated voltage at motor terminals.

4.01.03	The motor shall be designed to withstand momentary overload of 60% of full load torque for 15 sec without any damage.

4.02.00	Starting Requirements

4.02.01	Motor shall be designed for direct on line starting at full voltage. Starting current shall not exceed the limits set in IS/IEC.

4.02.02	The motor shall be capable of withstanding the stresses imposed if started at 110% rated voltage. The motor shall be designed to withstand 120% rated speed for two minutes without any mechanical damage.

4.02.03	Motor shall start with rated load and accelerate to full speed with 80% rated voltage at motor terminals.

4.02.04	a)	The motor shall be capable of three equally spaced starts in an hour, the motor initially being at a temperature not exceeding the rated load operating temperature.

b)	The motor shall be capable of two starts in succession with coasting to rest between starts and the motor initially at rated operating temperature.

4.02.05	Pump motor subject to reverse rotation shall be designed to withstand the stresses encountered when starting with shaft rotating at 125% rated speed in reverse direction.

4.03.00	Stress During Bus Transfer

4.03.01	The motor may be subjected to sudden application of 150% rated voltage during bus transfer, due to the phase difference between the incoming voltage and motor residual voltage.

4.03.02	The motor shall be designed to withstand any torsional and/or high current stresses which may result, without experiencing any deterioration in the normal life and performance characteristics.

4.04.00	Locked Rotor Withstand Time

4.04.01	The locked rotor withstand time under hot condition at 110% rated voltage shall be more than motor starting time by at least 2.5 seconds for motors upto 20 seconds starting time and by 5 seconds for motor with more than 20 seconds starting time.

4.04.02	Starting time mentioned above is at minimum permissible voltage of 80% rated voltage.

4.04.03	Hot thermal withstand curve shall have a margin of at least 10% over the full load current of the motor to permit relay setting utilizing motor rated capacity.

4.05.00	Enclosure

4.05.01	All motor enclosures shall conform to the degree of protection IP-55 unless otherwise specified.  Motor for outdoor or semi-outdoor service shall be of weather-proof construction.

4.05.02	For hazardous area approved type of increased safety enclosure shall be furnished.

4.06.00	Cooling

4.06.01	The motor shall be self ventilated type, either totally enclosed fan cooled (TEFC) or closed air circuit air cooled (CACA).

4.07.00	Winding and Insulation

4.07.01	All insulated winding shall be of copper.

4.07.02	All Motors shall have class F insulation but, limited to class B temperature rise.

4.07.03	Windings shall be impregnated to make them non-hygroscopic and oil resistant.

4.08.00	Tropical Protection

4.08.01	All motors shall have fungus protection involving special treatment of insulation and metal against fungus, insects and corrosion.

4.08.02	All fittings and hard wares shall be corrosion resistant.

4.09.00	Bearings

4.09.01	Motor shall be provided with antifriction bearings, unless sleeve bearings are required by the motor application.

4.09.02	Vertical shaft motors shall be provided with thrust and guide bearings. Thrust bearing of tilting pad type is preferred.

4.09.03	Bearings shall be provided with seals to prevent leakage of lubricant or entrance of foreign matters like dirt, water etc. into the bearing area.

4.09.04	Sleeve bearings shall be split type, ring oiled, with permanently aligned, close running shaft sleeves.

4.09.05	Grease lubricated bearings shall be pre lubricated and shall have provisions for in-service positive lubrication with drains to guard against over lubrication.

4.09.06	Oiled bearing shall have an integral self cooled oil reservoir with oil ring inspection ports, oil sight glass with oil level marked for standstill and running conditions and oil fill and drain plugs.

4.09.07	Forced lubricated or water cooled bearing shall not be used without prior approval of Owner.

4.09.08	Lubricant shall not deteriorate under all service conditions. The lubricant shall be limited to normally available types with IOC equivalent.

4.09.09	Bearings shall be insulated as required to prevent shaft current and resultant bearing damage.

4.10.00 	Noise & Vibration

4.10.01	The noise level shall not exceed 85 dB (A) at 1.5 meters from the motor.

4.10.02	The peak amplitude of the vibration shall be within I.S/IEC specified limits.

4.11.00	Motor Terminal Box

4.11.01	Motor terminal box shall be detachable type and located in accordance with Indian Standards clearing the motor base-plate/foundation

4.11.02	Terminal box shall be capable of being turned 360o in steps of 90o, unless otherwise approved.

4.11.03	The terminal box shall be split type with removable cover with access to connections and shall have the same degree of protection as motor.

4.11.04	The terminal box shall have sufficient space inside for termination/ connection of XLPE (1100V grade) insulated armoured Copper cables.

4.11.05	Terminals shall be stud or lead wire type, substantially constructed and thoroughly insulated from the frame.

4.11.06	The terminals shall be clearly identified by phase markings, with corresponding direction of rotation marked on the non-driving end of the motor.

4.11.07	The terminal box shall be capable of withstanding maximum system fault current for a duration of 0.25 sec.

4.11.08	Motor terminal box shall be furnished with suitable cable lugs and double compression brass glands.

4.11.09	In case of motor terminal box being not suitable for specified cable size/number, suitable adopter box/extension box shall be provided.

4.12.00	Grounding

4.12.01	The frame of each motor shall be provided with two separate and distinct grounding pads complete with tapped hole, GI bolts and washer.

4.12.02	The cable terminal box shall have a separate grounding pad for termination of grounding conductor.

4.13.00	Rating Plate

In addition to the minimum information required by IS, the following information shall be shown on motor rating plate :

a)	Temperature rise in oC under rated condition and method of measurement.

b)	Degree of protection.

c)	Bearing identification no. and recommended lubricant.

d)	Location of insulated bearings.

4.14.00	Accessories

4.14.01	General

Accessories shall be furnished, as listed below, or if otherwise required by driven equipment specification or application.

4.14.02	Space Heater

a)	Motor of rating 30KW and above shall be provided with space heaters, suitably located for easy removal or replacement.

b)	The space heater shall be rated 240 V, 1 phase, 50 Hz and sized to maintain the motor internal temperature above dew point when the motor is idle.

4.14.03	Accessory Terminal Box

a)	All accessory equipment such as space heater, temperature detector, etc., shall be wired to and terminated in terminal boxes, separate from motor (power) terminal box.

b)	Accessory terminal box shall be completed with double compression brass glands and pressure type terminals.

4.14.04	Drain Plug

Motor shall have drain plugs so located that they will drain the water, resulting from the condensation or other causes from all pockets of the motor casing.

4.14.05	Lifting Provisions

Motor weighing 25 kg. or more shall be provided with eye bolt or other adequate provision of lifting.

4.14.06	Dowel Pins

The motor shall be designed to permit easy access for drilling holes through motor feet or mounting flange for installation of dowel pins after assembling the motor and driven equipment.

4.14.07	Painting

Motor including fan shall be painted with corrosion proof paints with colour shade 631 of IS-5.

4.15.00	Construction

4.15.01	Stator Core

The stator lamination shall be made of high-grade silicon / magnetic  steel sheet varnished on both sides and pressed to form rigid core.

4.15.02	Rotor

The rotor construction shall be such that in case of dislodging of the rotor bar from the end ring, it should not come out and hit the stator core/ stator winding and damage.

5.00.00	TESTS

Routine and Type Tests are to be conducted in presence of customer’s representative as per IS:325/IEC-60034 and required copies of test certificates are to be furnished for approval.

6.00.00	DRAWINGS, DATA & MANUALS

Drawings, data & manuals for the motors shall be submitted as indicated below:

6.01.00	Along with the bid

a)	List of the motors

b)	Individual motor data sheet as per format of the proposal data sheets.

c)	Scheme & write up on forced lubrication system, if any

d)	Type test report

6.02.00	After Award of the Contract

a)	Dimensional General Arrangement drawing

b)	Foundation Plan & Loading

c)	Cable end box details

d)	Space requirement for rotor removal

e)	Thermal withstand curves hot & cold

f)	Starting and speed torque characteristics at 80% & 100% voltage

g)	Complete motor data

h)	Erection & Maintenance Manual

- Test reports

DATA SHEET FOR ELECTRICAL MOTOR

A.	POWER SUPPLY REQUIRED

| # Supply | ###### Description | ###### Consumer |
| --- | --- | --- |
| L.T. Supply | 415V, 3 Phase, 4W, 50 Hz, effectively earthed. | Motors upto 160KW |

B.	PERMISSIBLE VOLTAGE AND FREQUENCY VARIATION

A.C. Supply

Voltage 		: 	± 10%

Frequency		:	± 5%

Combined voltage	:	10% (absolute sum)

& frequency

PREFERRED MAKE OF MOTOR:

- ABB	2) SIEMENS   3) CGL   4)   MARATHON

5)  HINDALCO’s LIST OF VENDORS